


�


	Foreign Solids Analysis


	Customer Name	York Service/JCI	Sample Number	RR043115-001


	Job Name	DuPont Experimental Stn	Customer Sample No.	7872sludge


	Job ID	DE1619001	Collection Date	7/16/2007


	Manufacturer	York	Collected By	Service Tech


	Model Number	YPCST22G46CXA	Receive Date	7/19/2007


	Serial Number	GLCM157836	Analysis Date	7/20/2007


	Equipment Name	GLCM157836 sludge


	Equipment ID	DE1619001005


	Sample Description:	Amber Crystals


	Sample Data


	Iron	1	wt%


	Copper	9	wt%


	Zinc	< 1	wt%


	Magnesium	< 1	wt%


	Calcium	2	wt%


	Lead	< 1	wt%


	Molybdenum	< 1	wt%


	Phosphorus	1	wt%


	Boron	7	wt%


	Silver	< 1	wt%


	Chromium	< 1	wt%


	Cadmium	< 1	wt%


	Arsenic	< 1	wt%


	Silicon	68	wt%


	Barium	< 1	wt%


	Sodium	8 	wt%


	Potassium	3	wt%





	The particulates were dissolved in Aqua Regia and analyzed by ICP.


	Results are calculated relatively based on the total response of the instrument.


This report is based on a single sample. Sampling regularly and tracking the data provides the clearest insight to the solution 


chemistry of your unit. A large change in any result may make a resample advisable.


