
         



 SHAPE  \* MERGEFORMAT 
                                   
· 
                                                                             To: 
  Tom Sliwinski   

                                                                             Company:  DuPont Experimental Station

                                                                             Fax:
  302-695-7775
                                                                             Date: 
  07/17/08

Dear Tom,

The following work has already been performed on ABS #2 in order it keep it operational.

We offer to furnish the equipment and services specified herein, at prices stated and in accordance with Johnson Controls, Inc. Standard Terms and Conditions. Pricing good for 30 Days from date of proposal.

Johnson Controls is pleased to submit this proposal for your review: The following is a scope of work to be performed at the: DuPont Experimental Station 

Scope:

ABS #2

· Replace Defective Purge Pressure Transducer

· Replace Defective Leaving Chilled Water Temperature Sensor 

Price: $937.00

Johnson Controls is pleased to submit this proposal for your review: The services detailed herein will be performed by qualified York Factory trained Technicians, between the hours of 8:00 a.m. to 4:30 p.m. Monday through Friday. 
Upon your approval, please forward your purchase order by fax to my attention so that work can begin. Any questions please call my cell phone at 302-275-4797 (Fax 302-996-0461).

Regards,

Kevin M. Fraze

Service Technician

Joe Reilly                                                                                Jeff Collins

Service Sales Representative                                                Area Manager Delmarva

Accepted by: _______________________________

P.O.              _______________________________

Date:             ________________________________                                                                


_1263627887.doc
[image: image1.png]Johnson ﬂ/)l(,

Controls







