
__________________________________________________________________________________
Master Specification Note - Delete this page before use
__________________________________________________________________________________


[image: image1.wmf]
ABB Inc.

Effective June 15, 2012

ACH550-PNPT02U-EN REV. E
Condensed Sample Specification for

Variable Frequency Drives 

For HVAC Applications

To remove formatting restrictions use password: ABBHVAC - not recommended
Example styles in this document per CSI Master/Section/Page specifications. Sub paragraphs levels 5 and 6 are added to compensate for all 9 multi-list level styles in Microsoft Word
PART 1 -  Part 

1.01 Part  | Article
A. Part | Article | Paragraph
1. Part | Article | Paragraph | Sub 1
a. Part | Article | Paragraph | Sub 2

1) Part | Article | Paragraph | Sub 3

a) Part | Article | Paragraph | Sub 4

(1) Part | Article | Paragraph | Sub 5

(a) Part | Article | Paragraph | Sub 6

__________________________________________________________________________________
Master Specification Note: This guide specification is written according to the Construction Specifications Institute (CSI) Format. The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project. Coordinate this section with VFD schedule, other specification sections and the drawings.
__________________________________________________________________________________

HEATING, VENTILATING & AIR CONDITIONING [23 ## ##]

VARIABLE FREQUENCY DRIVES
PART 2 -  GENERAL

2.01 DESCRIPTION

A. This specification is to cover a complete Variable Frequency Drive consisting of a pulse width modulated (PWM) inverter designed for use with a standard NEMA Design B induction motor.

B. The drive manufacturer shall supply the drive and all necessary options as herein specified.  VFDs that are manufactured by a third party and “brand labeled” shall not be acceptable. All VFDs installed on this project shall be from the same manufacturer.

2.02 QUALITY ASSURANCE

A. Referenced Standards and Guidelines:

1. IEEE 519-1992, Guide for Harmonic Content and Control.
2. UL508(A)(C)
3. ICS 7.0, AC Adjustable Speed Drives

4. EN/IEC 61800-3

5. NEC 430.120, Adjustable-Speed Drive Systems

6. IBC 2012 Seismic – referencing ASC 7-05 and ICC AC-156

B. Qualifications:

1. VFDs and options shall be UL508 listed as a complete assembly.  The base VFD shall be UL listed for 100 kA SCCR without the need for external input fuses.
2. CE Mark – The base VFD shall meet product standard EN 61800-3 for the First Environment restricted level (Category C2).  (RFI / EMI Filter spec).

3. The entire VFD assembly, including the bypass (if specified), shall be seismically certified and labeled as such in accordance with the 2012 International Building Code (IBC):

a. VFD manufacturer shall provide Seismic Certification and Installation requirements at time of submittal.

b. Seismic importance factor of 1.5 rating is required, and shall be based upon actual shake test data as defined by ICC AC-156.

c. Seismic ratings based upon calculations alone are not acceptable. Certification of Seismic rating must be based on testing done in all three axis of motion by a certified lab.

d. Special seismic certification of equipment and components shall be provided by OSHPD preapproval.

2.03 SUBMITTALS

A. Submittals shall include the following information:

1. Outline dimensions, conduit entry locations and weight.

2. Customer connection and power wiring diagrams.

3. Complete technical product description include a complete list of options provided.  

2.04 BUILDING INFORMATION MODELING (BIM)

A. BIM objects shall contain IFC parameters and associated data applicable to building system requirements. These elements shall support the analytic process including size, clearance, location, mounting heights, and system information where applicable. 

PART 3 -  PRODUCTS

3.01 VARIABLE FREQUENCY DRIVES

A. The VFD package as specified herein and defined on the VFD schedule shall be enclosed in a UL Type enclosure (enclosures with only NEMA ratings are not acceptable). 

1. Environmental operating conditions: -15 to 40° C (5 to 104° F) continuous. Altitude 0 to 3300 feet above sea level, less than 95%, non-condensing All circuit boards shall be coated to protect against corrosion.
B. All VFDs shall have the following standard features.

1. All VFDs shall have the same customer interface, including digital display, and keypad, regardless of horsepower rating.  The keypad shall be removable, capable of remote mounting and allow for uploading and downloading of parameter settings as an aid for start-up of multiple VFDs. 

2. The keypad shall include Hand-Off-Auto selections and manual speed control.  There shall be fault reset and “Help” buttons on the keypad.  The Help button shall include “on-line” assistance for programming and troubleshooting.  

3. VFDs through 200 HP shall have internal chokes (reactors) providing 5% impedance to reduce the harmonics to the power line and to add protection from AC line transients.
4. The input current rating of the VFD shall not be greater than the output current rating.  VFD’s with higher input current ratings require the upstream wiring, protection devices, and source transformers to be oversized per NEC 430.122
5. The VFD shall provide a programmable loss-of-load (broken belt / broken coupling) Form-C relay output.  The drive shall be programmable to signal the loss-of-load condition via a keypad warning, Form-C relay output, and / or over the serial communications bus.  
C. All VFDs to have the following adjustments:

1. Run permissive circuit - There shall be a run permissive circuit for damper or valve control.  Regardless of the source of a run command (keypad, input contact closure, time-clock control, or serial communications), the VFD shall provide a dry contact closure that will signal the damper to open (VFD motor does not operate).  When the damper is fully open, a normally open dry contact (end-switch) shall close.  The closed end-switch is wired to a VFD digital input and allows VFD motor operation.  Two separate safety interlock inputs shall be provided.  When either safety is opened, the motor shall be commanded to coast to stop and the damper shall be commanded to close.  

2. The VFD control shall include a programmable time delay for VFD start and a keypad indication that this time delay is active.  A Form C relay output provides a contact closure to signal the VAV boxes open.  This will allow VAV boxes to be driven open before the motor operates
3. The VFD shall include a fireman’s override input.  The mode shall override all other inputs (analog/digital, serial communication, and all keypad commands), except customer defined safety run interlocks, and force the motor to run at a preset speed or in a separate PID mode.  

D. Serial Communications

1. The VFD shall have an EIA-485 port as standard.  The standard protocols shall be Modbus, Johnson Controls N2, Siemens Building Technologies FLN, and BACnet.  The use of third party gateways and multiplexers is not acceptable.  All protocols shall be “certified” by the governing authority (i.e. BTL Listing for BACnet).  
E. EMI / RFI filters.  All VFD’s shall include EMI/RFI filters.  The onboard filters shall allow the VFD assembly to be CE Marked and the VFD shall meet product standard EN 61800-3 for the First Environment restricted level (Category C2).
F. DRIVE OPTIONS – Options shall be furnished and mounted by the drive manufacturer as defined on the VFD schedule.  All optional features shall be UL Listed by the drive manufacturer as a complete assembly and carry a UL508 label.
G. BYPASS – Bypasses shall be furnished and mounted by the drive manufacturer as defined on the VFD schedule.  All VFD with bypass configurations shall be UL Listed by the drive manufacturer as a complete assembly and carry a UL508 label. 
1. A complete factory wired and tested bypass system consisting of a door interlocked, padlockable circuit breaker, output contactor, bypass contactor, and fast acting VFD input fuses.  UL Listed motor overload protection shall be provided in both drive and bypass modes.

2. The bypass enclosure door and VFD enclosure must be mechanically interlocked such that the disconnecting device must be in the “Off” position before either enclosure may be accessed.

3. The VFD and bypass package shall have a UL listed short circuit current rating (SCCR) of 100,000 Amps and this rating shall be indicated on the UL data label.
4. The bypass shall maintain positive contactor control through the voltage tolerance window of nominal voltage +30%, -35%.  This feature is designed to avoid contactor coil failure during brown out / low line conditions and allow for input single phase operation when in the VFD mode.  Designs that will not allow input single phase operation in the VFD mode are not acceptable.

5. Motor protection from single phase power conditions - the bypass system must be able to detect a single phase input power condition while running in bypass, disengage the motor in a controlled fashion, and give a single phase input power indication.  Bypass systems not incorporating single phase protection in bypass mode are not acceptable.

6. The bypass system shall be designed for stand-alone operation and shall be completely functional in both Hand and Automatic modes even if the VFD has been removed from the system for repair / replacement.  Serial communications shall remain functional even with the VFD removed.  Bypass systems that do not maintain full functionality with the drive removed are not acceptable.

7. Serial communications – the bypass shall be capable of being monitored and / or controlled via serial communications.  On-board communications protocols shall include ModBus RTU; Johnson Controls N2; Siemens Building Technologies FLN (P1); and BACnet MS/TP.  

8. The user shall be able to select the text to be displayed on the keypad when an external safety opens.  Example text display indications include “FireStat”, “FreezStat”, “Over pressure” and “Low suction”.  The user shall also be able to determine which of the four (4) safety contacts is open over the serial communications connection. 

9. Smoke Control Override Mode (Override 1) – The bypass shall include a dedicated digital input that will transfer the motor from VFD mode to Bypass mode upon receipt of a dry contact closure from the Fire / Smoke Control System.  The Smoke Control Override Mode action is not programmable and will always function as described in the bypass User’s Manual documentation.   In this mode, the system will ignore low priority safeties and acknowledge high priority safeties.  All keypad control, serial communications control, and normal customer start / stop control inputs will be disregarded.  This Smoke Control Mode shall be designed to meet the intent of UL864/UUKL.

10. Fireman’s Override Mode (Override 2) – the bypass shall include a second, programmable override input which will allow the user to configure the unit to acknowledge some digital inputs, all digital inputs, ignore digital inputs or any combination of the above.  This programmability allows the user to program the bypass unit to react in whatever manner the local Authority Having Jurisdiction (AHJ) requires.  The Override 2 action may be programmed for “Run-to-Destruction”.  The user may also force the unit into Override 2 via the serial communications link.

PART 4 -  EXECUTION

4.01 INSTALLATION

A. Installation shall be the responsibility of the mechanical contractor.  
B. Power wiring shall be completed by the electrical contractor, to NEC code 430.122 wiring requirements based on the VFD input current.  
C. The contractor shall complete all wiring in accordance with the recommendations of the VFD manufacturer as outlined in the installation manual.

4.02 START-UP

A. Factory start-up shall be provided for each drive by a factory authorized service center.  

4.03 PRODUCT SUPPORT

A. Factory trained application engineering and service personnel that are thoroughly familiar with the VFD products offered shall be locally available at both the specifying and installation locations.  A toll free 24/365 technical support line connected to factory support personnel located in the US shall be available. Technical support offered only through the local sales office is not acceptable.

4.04 WARRANTY

A. The VFD Product Warranty shall be 36 months from the date of factory shipment.  The warranty shall include all parts, labor, travel time and expenses.  A toll free 24/365 technical support line shall be available.

End of Section
September 6, 2012

[Project Name]
Variable Frequency Drives [23 ## ##] Page 1

_1403432229

