VLT 6000 Start-Up Check List

	
	1. Reference Material

	
	a. VLT 6000 Installation, Operation and Maintenance Manual.

	
	b. Customer Connection Diagram (specific for the order).

	
	c. Schematic Diagram (specific for the order).

	
	2. Pre-Installation Checks

	
	a. Compare the drive model number to what was ordered.

	
	b. Be sure the following are for the same voltage:

	
	i) Drive.

	
	ii) Power line.

	
	iii) Motor.

	
	c. Record the following motor data:

	
	i) Voltage.

	
	ii) Frequency.

	
	iii) Full load current.

	
	iv) Full load speed.

	
	v) Power (convert HP to kW — see the description of parameter 102).

	
	d. Be sure that rated drive current is greater than or equal to the total full load current of all motors which will be driven at once.

	
	e. Check motor wiring.

	
	i) A disconnect between the drive and the motor should be interlocked to the drive or else nuisance trips may occur.

	
	ii) No power factor correction capacitors between the drive and the motor.

	
	iii) Two speed motors must be wired permanently for full speed.

	
	iv) Y-start — (-run motors must be wired permanently for run.

	
	v) Part winding start motors must be wired permanently for run.

	
	3. Installation Checks

	
	a. Input fusing for the drive must be provided.

	
	b. Environmental concerns — standard NEMA 1 drive.

	
	i) Clean.

	
	ii) Dry (max 95% relative humidity, non-condensing).

	
	iii) 14oF to 104oF ambient temperature (some drives have a wider range).

	
	iv) 3,300 foot maximum elevation with no derating.

	
	c. Mounting

	
	i) Vertical.

	
	ii) No heat sink fins exposed out the back.

	
	iii) See the Instruction Manual for mounting clearances.

	
	iv) Keep construction dirt out of the drive.

	
	d. Wiring

	
	i) Separate conduits must be provided for input power, output power, and control wiring.

	
	ii) Note that the safety interlock and remote run/stop circuitry for drives with bypasses is 115 V AC.

	
	iii) Use knock-outs or conduit entry plates. Avoid metal shavings in cabinets.

	
	iv) Protect signal wires from noise.

	
	v) Ground each drive individually.

	
	vi) Double check input and output power wiring for correct location.

vii) Check all electrical connections that are visible to insure they are tight.

viii) Clean the interior of the drive or bypass cabinet to insure proper drive cooling and reduce potential corrosion damage.

	
	4. Setting Up the Drive for the Motor — This step is essential!

	
	a. Parameter 101

	
	i) If one motor is connected to the drive at a time, set this to AEO FUNCTION.

	
	ii) Otherwise set this to MULTIPLE MOTORS. (Parameter 108, MULTIPLE MOTOR STARTING VOLTAGE should be adjusted later to provide reliable starts and minimum starting current.)

	
	b. Parameter 102, MOTOR POWER (in kW).

	
	c. Parameter 103, MOTOR VOLTAGE.

	
	d. Parameter 104, MOTOR FREQUENCY.

	
	e. Parameter 105, MOTOR CURRENT

	
	f. Parameter 106, MOTOR SPEED.

	
	g. Parameter 118, MOTOR PWR FACT. Important for 6- and 8-pole motors.

	
	h. Parameter 107, run AUTOMATIC MOTOR ADAPTATION (if desired).

	
	5. Check Parameter Settings

	
	a. Parameter 201, MIN. FREQUENCY (6 Hz for fans, 18 Hz for pumps)

	
	b. Parameter 202, MAX. FREQUENCY (60 Hz)

	
	c. Parameter 206, RAMP UP TIME (60 sec for fans, 10 sec for pumps)

	
	d. Parameter 207, RAMP DOWN TIME (60 sec for fans, 10 sec for pumps)

	
	e. Parameter 208 AUTORAMPING (ENABLE)

	
	6. Operational Tests — HAND

	
	a. Check the motor’s rotation from the drive. If incorrect, reverse two leads between the drive and the motor.

	
	b. If a bypass is provided, check the motor’s rotation in bypass mode. If incorrect, reverse two input power lines.

	
	c. Accelerate the motor quickly to full speed and verify operation.

	
	d. Decelerate the motor quickly to a stop and verify operation.

	
	e. Slowly operate the motor over the entire speed range and check for resonance.

	
	7. Operational Tests — AUTO, Open Loop

	
	a. Parameter 204, MIN. REFERENCE (usually the same as parameter 201)

	
	b. Parameter 205, MAX. REFERENCE (usually the same as parameter 202)

	
	c. Ensure that the drive follows run/stop commands from the system.

	
	d. Ensure that the drive follows the speed command from the system.

	
	8. Operational Tests — Auto, Closed Loop

	
	a. Set up the PID control parameters as required.

	
	b. Ensure that the drive follows run/stop commands from the system.

	
	c. Ensure that the drive responds to the feedback signal from the system.

	
	9. Final Adjustments

	
	a. Use parameters 109 and 216 through 220 to correct any resonance problems.

	
	b. Set up parameter 402, FLYING START, as required.

	
	c. Special control features, as required.

	
	d. Lock out keypad functions as required.

	
	e. Copy parameters to other setups as required.

	
	f. Copy parameters to the LCP.

	
	g. Lock out parameter changes as required.



12/03/02

