    [image: image1.png]/
sommson J( ;ayORK METASYS® Frick
Controls FACTORY SERVICE rromamames | 7 |
SABROE |

B JoHNsON
LIRES!




                         Site Vacuum Test Certificate

	Client:
	                                                                      Chiller #

	
	

	Location:
	

	
	

	Contract No.:
	

	
	

	Refer to Evacuation Test instructions in the York IOM manual.

	
	

	Required Vacuum Hold
	5 mm
	Microns HG Abs / m Bar A   for 8  Hours

	
	
	

	Rise:
	1.3mm
	Microns HG Abs / m Bar A   in 8 Hours

	
	

	
	

	Actual Vacuum Hold
	
	

	
	
	
	
	Temperature
	

	Date and Time
	
	
	Microns HG Abs / (m Bar A)
	
	°F / °C

	
	
	
	
	
	

	Date and Time
	
	
	Microns HG Abs/ (m Bar A)
	
	°F / °C

	
	

	
	

	
	
	

	NOTE:
It is recommended that the system be evacuated to 5000 microns absolute pressure (5mm) with a maximum pressure rise of 1300 microns (1.3mm) in an eight hour test period.

	
	

	 If test holds, evacuation will continue until a vacuum level of below 1000 microns (1mm) is reached.

	
	

	
	

	
	

	Signed
	
	Print
	
	Customer Rep

	
	
	
	
	

	
	
	
	
	

	Signed
	
	Print
	
	JCI/YORK  Rep

	
	

	
	
	

	
	Date:
	
	

	
	
	


