	YORK PROCESS SYSTEMS - APPLICATION ENGINEERING STANDARD

QUANTUM LX SETPOINT SHEET
	AES 1300.07
ISSUE: 31 MAY 05



[image: image11.jpg]



QUANTUM LX
CONTROL PANEL

SETPOINT / CONFIGURATION DATA SHEETS

	CUSTOMER:
	     

	PURCHASER:
	     

	
	     

	
	     

	
	     

	
	

	YORK SALES ORDER
	       REV  FORMDROPDOWN 

	PURCHASER SALES ORDER
	     


IMPORTANT: This manual is provided for recording the screen display settings that are entered for Quantum LX control panel installations at start-up. Please file for future reference.

All values or setpoints in the SETPOINT DATA SHEET that are NOT filled in will be at the DEFAULT value or setpoint.
Version 6.61
September 5, 2008
Johnson Controls, Inc - ECS

200 N. Franklin St., PO Box 997

Waynesboro, Pennsylvania USA 17268-0997

Phone: (717) 762-2121

Fax: (717) 762-0654

TABLE OF CONTENTS
MENU STRUCTURE……………………………………………………………..……………………………….…………………………3
NOTES………………………………………………………………………….……..………………………………………………………4

SETPOINT SHEET NOTES………………………………………….…………..………………………………………………4

PROJECT SPECIFIC SETPOINT SHEET NOTES………………….……………….………………………………………..4
ABOUT
…………………………………………………………………………….…………………………………………………………5
SESSION…………………………………………………………………..……….…………………………………………………………5
CONFIGURATION……………………………………………………………….…………………………..………………………………5

COMPRESSOR………………………………………………………….……………...…………………………………………5

COMMUNICATIONS……………………………………………………………...………………………………………………6

ETHERNET…………………………………………………………………………………...……………………………………7

DIGITAL I/O…………………………………………………………………...……………...……………………………………8


PAGE 1…………………………………………………………………..………………………………………………8


PAGE 2…………………………………………………………………………………..………………………………8


PAGE 3…………………………………………………………………………………………………..………………8
CALIBRATION
………………………………………………………………………………...………………………………………9-19

PRESSURE………………………………………………………………………….…………………………………………9-10

TEMPERATURE……………………………………………………………...………...……………………………………11-12

CAPACITY / VOLUME…………………………………………………..………………………………………………………12

MOTOR / MISCELLANEOUS………………………………………..…………………………………………………………13

PHD……………………………………………………………………………………………..…………………………………14

ANALOG OUTPUTS………………………………………………….......…………………………………………………15-16


RETRANSMITTING OUTPUTS…………………………………………………………….…..……………………15


VFD CONDENSER ANALOG OUTPUTS………………………………………………..…………………………16

AUXILIARIES…………………………………………………………………………………………………………………16-19


PAGE 2…………………………………………………………………………..…………………………………16-17


PAGE 1……………………………………………………………………………..………………………………18-19
SETPOINTS………………………………………………………………………………………………..……………………………20-43

CAPACITY CONTROL SETPOINTS………………………………………………...….…………………………………20-23


MODE 1………………………………………………………………….…………..…………………………………20


MODE 2………………………………………………………………….…………………..…………………………21


MODE 3………………………………………………………………….…………..…………………………………22


MODE 4……………………………………………………………….……………..…………………………………23

SEQUENCING……………………………………………………………..…………………………………………………24-27


SYSTEM 1………………………………………………………………………….…..………………………………24


SYSTEM 2………………………………………………………………..……….……………………………………25



SYSTEM 3……………………………………………………………..………….……………………………………26


SEQUENCING CONTROL……………………………………………..…………………………….………………27

COMPRESSOR SAFETIES…………………………………………………………………………………………….………28

PACKAGE SAFETIES………………………………………………………………………………………………………29-30

DRIVE : ELECTRIC MOTOR…………………………………………………………………...………………………………30

DRIVE : ENGINE OR TURBINE...................................................................................................................................31

CAPACITY POSITION…………………………………………………………………………………………………………..32

CONDENSER…………………………………………………………………………………………………………………….32


CONDENSER DIGITAL CONTROL……………………………………………………….………………………...32


CONDENSER ANALOG CONTROL……………………………………………………….………………………..32

MISCELLANEOUS…………………………………………...………………………………………………………………….33

SCHEDULING……………………………………………………...…………………………………………………………….33

PHD MONITORING……………………………………………………………………………………………………………...34

PID SETUP……………………………………………………………………………………………………………………35-36


PAGE 1…………………………………………………………………………..……………………………………..35


PAGE 2……………………………………………………………………………………..…………………………..36

SUPERHEAT CONTROL SETUP……………………………………………………………………………………………...37

PANEL…………………………………………………………………………...………………………………………………..38

AUXILIARIES…………………………………………………………………………………………………………………38-43


ANALOG INPUTS………………………………………………….………………………………………………38-40



PAGE 1………………………………………………………………………….……………………….38-39



PAGE 2…………………………………………………………………………………………………..39-40


DIGITAL INPUT CONFIGURATION………………………………………………………………………………...41


DIGITAL OUTPUT CONFIGURATION………………………………………………………………………….42-43
[image: image1.emf][image: image2.png]


MENU STRUCTURE

SETPOINT SHEET NOTES

The title structure of each table in this setpoint sheet is made to reflect the destination of each table in the Quantum LX programming structure.  

Example: MAIN MENU / SUBMENU / SUBMENU / SUBMENU

This setpoint sheet should be followed page by page to correctly configure the Quantum LX.  Some tables are out of order in this setpoint sheet.  An example of this is the auxiliary analog setup pages found in the Calibration Main Menu / auxiliaries submenu.  This setpoint sheet will display page 2 first followed by page 1.  In order to correctly setup the auxiliary analogs in the Quantum LX, page 2 should be configured first followed by page 1.  
PROJECT SPECIFIC SETPOINT SHEET NOTES
     

SETPOINT DATA SHEETS
Quantum™ LX Version 6.61 (09/05/2008) XE "SETPOINT DATA SHEETS" 
In most cases, updating software XE "software"  on the Quantum™ LX panel will require clearing the current setpoints and data stored in the nonvolatile memory XE "memory"  on the main board. It is suggested that the operator first record all control setpoints prior to performing program upgrades.  XE "Panel Setup" 

 XE "Factory Setup" The setpoint data sheets XE "setpoint data sheets"  are useful for recording this information.

ABOUT
	Description
	Value
	Default
	Range
	Units

	Sales Order
	     
	0
	0 to 9999999
	None

	Item 
	     
	0
	0 to 99999
	


SESSION
	Description
	Value
	Default
	Range
	Units

	User Level
	     
	0
	
	

	Password
	     
	None
	
	

	Language
	 FORMDROPDOWN 

	English
	*
	

	Pressure Units
	 FORMDROPDOWN 

	PSIG
	*
	

	Temperature Units
	 FORMDROPDOWN 

	F
	*
	

	Date Format
	 FORMDROPDOWN 

	US
	*
	


         * Refer to S90-021 O or S90-022 O (Operation) for additional information
CONFIGURATION / COMPRESSOR
	Control
	Description
	Value
	Default
	Range
	Units

	Misc.
	Sequencing
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	Condenser
	 FORMDROPDOWN 

	Disabled
	
	

	
	Screen Saver
	     
	15
	0 to 60
	Time
	MIN

	Capacity
	Mode 1
	Disabled / Enabled
	 FORMDROPDOWN 

	Enabled
	Disabled or Enabled
	None

	
	
	Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Suction Pressure
	None
	

	
	
	Direction
	 FORMDROPDOWN 

	Forward
	Forward or Reverse
	

	
	Mode 2
	Disabled / Enabled
	 FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Direction
	 FORMDROPDOWN 

	Forward
	Forward or Reverse
	

	
	Mode3 
	Disabled / Enabled
	 FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Direction
	 FORMDROPDOWN 

	Forward
	Forward or Reverse
	

	
	Mode 4
	Disabled / Enabled
	 FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Disabled
	Disabled or Enabled
	

	
	
	Direction
	 FORMDROPDOWN 

	Forward
	Forward or Reverse
	

	Package
	Compressor
	 FORMDROPDOWN 

	RWF
	None
	

	
	Pump
	 FORMDROPDOWN 

	No Pump
	
	

	
	Dual Pump
	 FORMDROPDOWN 

	Disabled
	
	

	
	Drive
	  Screw Compressor With:  
 FORMDROPDOWN 

	Screw w/Constant Electric
	
	

	
	Refrigerant
	 FORMDROPDOWN 
    FORMDROPDOWN 

	R717
	
	

	
	Filter
	 FORMDROPDOWN 

	Disabled
	
	

	
	Power Pac
	 FORMDROPDOWN 

	No
	
	


CONFIGURATION / COMMUNICATIONS
	Control
	Description
	Value
	Default
	Range
	Units

	Compressor ID
	
	     
	0
	0 to 99
	* None

	Map File
	Should Map File Be Used
	 FORMDROPDOWN 

	No
	*
	

	Comm 1
	Baud rate
	 FORMDROPDOWN 

	19200
	*
	

	
	Data Bits
	     
	8
	7 to 8
	

	
	Stop Bits
	     
	1
	1 to 2
	

	
	Parity
	 FORMDROPDOWN 

	None
	*
	

	
	Protocol
	 FORMDROPDOWN 

	
	
	

	Comm 2
	Baud rate
	 FORMDROPDOWN 

	19200
	
	

	
	Data Bits
	     
	8
	7 to 8
	

	
	Stop Bits
	     
	1
	1 to 2
	

	
	Parity
	 FORMDROPDOWN 

	None
	*
	

	
	Protocol
	 FORMDROPDOWN 

	
	
	

	Comm 3
	Baud rate
	 FORMDROPDOWN 

	19200
	
	

	
	Data Bits
	     
	8
	7 to 8
	

	
	Stop Bits
	     
	1
	1 to 2
	

	
	Parity
	 FORMDROPDOWN 

	None
	*
	

	
	Protocol
	 FORMDROPDOWN 

	
	
	


* Refer to S90-021 O, S90-022 O (Operation) or S90-020 CS (Communications Setup) for additional information

CONFIGURATION / ETHERNET

	Control
	Description
	Value
	Default
	Range
	Units

	IP Data
	Address Type
	 FORMDROPDOWN 

	Fixed (Static) 
	None 
	None

	
	IP Address
	     
	192
	0.0 to 255.0
	

	
	
	     
	168
	
	

	
	
	     
	0
	
	

	
	
	     
	83
	
	

	
	Gateway 
Address
	     
	192
	
	

	
	
	     
	168
	
	

	
	
	     
	0
	
	

	
	
	     
	1
	
	

	
	Subnet Mask
	     
	255
	
	

	
	
	     
	255
	
	

	
	
	     
	255
	
	

	
	
	     
	0
	
	

	
	Web Server Port
	     
	80
	0.0 to 99999.0
	

	Naming Data
	Hostname
	     
	QLX-Host
	None 

	
	Workgroup
	     
	QLX Compressors
	


	
	Comment
	     
	
	

	Email Data
	Email Notification On Shutdown
	 FORMDROPDOWN 


	
	Local Email Address
	     

	
	Alias Name For Local Email Address
	     

	
	Subject
	     

	
	SMTP Server Name OR IP Address
	     

	
	SMTP Server Port Number
	  25  

	
	Comma-Delimited List Of Email Recipients
	     

	Protocols
	ModBus TCP
	 FORMDROPDOWN 

	Disabled
	None

	
	  Ethernet/IP
	 FORMDROPDOWN 

	Disabled
	

	
	PROFINET
	 FORMDROPDOWN 

	Disabled
	


CONFIGURATION / DIGITAL I/O / PAGE 1

	Input / Output
	IO Board
	IO Channel
	Input / Output
	IO Board
	IO Channel

	  Oil Level Switch  
	 FORMDROPDOWN 

	  13  
	  Economizer  
	 FORMDROPDOWN 

	  11  

	  Capacity Decrease  
	 FORMDROPDOWN 

	  6  
	  Liquid Injection  
	 FORMDROPDOWN 

	  9  

	  Capacity Increase  
	 FORMDROPDOWN 

	  5  
	  Oil Heater  
	 FORMDROPDOWN 

	  21  

	  Volume Decrease  
	 FORMDROPDOWN 

	  8  
	  Hot Gas Bypass  
	 FORMDROPDOWN 

	  16  

	  Volume Increase  
	 FORMDROPDOWN 

	  7  
	  Comp. Mtr. Start Signal  
	 FORMDROPDOWN 

	  1  

	  Capacity Step #1  
	 FORMDROPDOWN 

	  0  
	  Comp. Mtr. Starter Feedback  
	 FORMDROPDOWN 

	  2  

	  Capacity Step #2  
	 FORMDROPDOWN 

	  0  
	  Oil Pump Start Signal  
	 FORMDROPDOWN 

	  3  

	  Capacity Step #3  
	 FORMDROPDOWN 

	  0  
	  Oil Pump Feedback  
	 FORMDROPDOWN 

	  4  

	  Capacity Step #4  
	 FORMDROPDOWN 

	  0  
	  Full Flow Pump Start Signal  
	 FORMDROPDOWN 

	  0  

	  Capacity Step #5  
	 FORMDROPDOWN 

	  0  
	  Oil Pump #2 Start Signal  
	 FORMDROPDOWN 

	  15  

	  Capacity Step #6  
	 FORMDROPDOWN 

	  0  
	  Oil Pump #2 Feedback  
	 FORMDROPDOWN 

	  16  

	  Capacity Step #7  
	 FORMDROPDOWN 

	  0  
	


CONFIGURATION / DIGITAL I/O / PAGE 2

	Input / Output
	IO Board
	IO Channel
	Input / Output
	IO Board
	IO Channel

	  High Liquid Lvl Shutdown  
	 FORMDROPDOWN 

	  13  
	  Remote Load  
	 FORMDROPDOWN 

	  4  

	  Mode Select A  
	 FORMDROPDOWN 

	  19  
	  Remote Unload  
	 FORMDROPDOWN 

	  5  

	  Mode Select B  
	 FORMDROPDOWN 

	  20  
	  Condenser Control Step 1  
	 FORMDROPDOWN 

	  21  

	  Shutdown  
	 FORMDROPDOWN 

	  23  
	  Condenser Control Step 2  
	 FORMDROPDOWN 

	  22  

	  Warning  
	 FORMDROPDOWN 

	  22  
	  Condenser Control Step 3  
	 FORMDROPDOWN 

	  23  

	  Balance Piston  
	 FORMDROPDOWN 

	  12  
	  Condenser Control Step 4  
	 FORMDROPDOWN 

	  24  

	  Panel Heater  
	 FORMDROPDOWN 

	  15  
	  Power Assist  
	 FORMDROPDOWN 

	  24  

	  Permissive Start  
	 FORMDROPDOWN 

	  17  
	  Dx Circuit #1  
	 FORMDROPDOWN 

	  19  

	  Ready To Run  
	 FORMDROPDOWN 

	  1  
	  Dx Circuit #2  
	 FORMDROPDOWN 

	  20  

	  Remote Enabled  
	 FORMDROPDOWN 

	  2  
	  Main Oil Injection  
	 FORMDROPDOWN 

	  0  

	  Recycle Delay  
	 FORMDROPDOWN 

	  6  
	

	  Remote Start/Stop  
	 FORMDROPDOWN 

	  3  
	


CONFIGURATION / DIGITAL I/O / PAGE 3

	Input / Output
	IO Board
	IO Channel
	Input / Output
	IO Board
	IO Channel

	  Liquid Level Increase  
	 FORMDROPDOWN 

	  0  
	  PLC Interlock  
	 FORMDROPDOWN 

	  0  

	  Liquid Level Decrease  
	 FORMDROPDOWN 

	  0  
	  High VI Liquid Injection  
	 FORMDROPDOWN 

	  10  


CALIBRATION / PRESSURE

(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	PSIG Conversion
	     
	14.7
	8.0 to 20.0
	Pressure
	PSIG

	Suction
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	0.0 to 985.3
	
	

	
	
	High
	     
	185.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	9
	
	

	Discharge
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	8
	
	

	Oil
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	6
	
	

	Balance Piston
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	10
	
	

	Main Oil Injection


	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	15
	
	


The following are the type of selectable inputs that are available for the device source, and signal selections:


        * Device Source 


** Sensor Signal Selections:

	None
	
	None
	4-20mA
	RTD
	Vibration

	Analog Board 1
	
	0-5V
	Pot.
	CT
	1-10V

	Analog Board 2
	
	1-5V
	ICTD
	RPM
	+/- 5V


CALIBRATION / PRESSURE (Continued)
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Economizer
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	System Discharge
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	11
	
	

	Filter
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG


	
	Range
	Low
	     
	-14.7
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3
	-14.7 to 985.3
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	7
	
	

	Manifold
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-30.0 to 30.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-14.7
	-14.7 to 130.3
	
	

	
	
	High
	     
	57.8
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	1-5V
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	3
	
	


The following are the type of selectable inputs that are available for the device source, and signal selections:


* Device Source 


** Sensor Signal Selections:
	None
	
	None
	4-20mA
	RTD
	Vibration

	Analog Board 1
	
	0-5V
	Pot.
	CT
	1-10V

	Analog Board 2
	
	1-5V
	ICTD
	RPM
	+/- 5V


CALIBRATION / TEMPERATURE

(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Suction
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	1
	
	

	Discharge
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	2
	
	

	Oil
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	3
	
	

	Separator
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	4
	
	

	Process Leaving
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	5
	
	


CALIBRATION / TEMPERATURE (CONTINUED)

(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Process Entering
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-92.2 to 92.2
	Temperature
	F

	
	Range
	Low
	     
	-459.4
	-1768 to 1832
	
	

	
	
	High
	     
	463.1
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	ICTD
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	4
	
	


The following are the type of selectable inputs that are available for the device source, and signal selections:



* Device Source 


** Sensor Signal Selections:

	None
	
	None
	4-20mA
	RTD
	Vibration

	Analog Board 1
	
	0-5V
	Pot.
	CT
	1-10V

	Analog Board 2
	
	1-5V
	ICTD
	RPM
	+/- 5V


CALIBRATION / CAPACITY VOLUME
	Control
	Description
	Value
	Default
	Range
	Units

	Capacity
	Sensor Signal
	 FORMDROPDOWN 

	4-20mA
	None
	None

	
	IO Board
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	IO Channel
	     
	14
	
	

	
	Travel
	     
	196.0
	0.0 to 500.0
	

	Volume
	  Sensor Signal
	 FORMDROPDOWN 

	4-20mA
	None
	

	
	IO Board
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	IO Channel
	     
	15
	
	

	
	Bottom Of Range
	     
	2.2
	0.0 to 10.0
	

	
	Top Of Range
	     
	5.0
	
	

	
	Dead Band
	     
	0.2
	0.0 to 2.0
	

	
	Minimum On Time
	     
	0.5
	0.0 to 5.0
	


CALIBRATION / MOTOR MISCELLANEOUS

	Control
	Description
	Value
	Default
	Range
	Units

	Motor Amps
	Current value
	     
	
	None
	None

	
	Sensor Signal **
	 FORMDROPDOWN 

	CT
	
	

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	16
	
	

	Kilowatts
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-500.0 to 500.0
	Kilowatts
	kW

	
	Range
	Low
	     
	0.0
	-1000.0 to 10000.0
	
	

	
	
	High
	     
	5000.0
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	4-20mA
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	16
	
	

	RPM
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-360.0 to 360.0
	Speed
	RPM

	
	Range
	Low
	     
	0.0
	-1000.0 to 6000.0
	
	

	
	
	High
	     
	3600 RPM
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	4-20ma
	None
	None


	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 2
	
	

	
	I/O Channel
	     
	16
	
	

	Remote Capacity Position
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-10.0 to 10.0
	Percent
	%

	
	Range
	Low
	     
	0.0
	-1000.0 to 1000.0
	
	

	
	
	High
	     
	100.0 %
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	4-20Ma
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	External Input
	Current value
	     
	
	None
	None

	
	Offset
	     
	0.0
	-75.0 to 75.0
	Pressure
	PSIG

	
	Range
	Low
	     
	-30.0
	-14.7 to 985.3
	
	

	
	
	High
	     
	485.3 PSIG
	
	
	

	
	Sensor Signal **
	 FORMDROPDOWN 

	4-20mA
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	12
	
	




* Device Source 


** Sensor Signal Selections:

	None
	
	None
	4-20mA
	RTD
	Vibration

	Analog Board 1
	
	0-5V
	Pot.
	CT
	1-10V

	Analog Board 2
	
	1-5V
	ICTD
	RPM
	+/- 5V


CALIBRATION / PHD

All RTD inputs must be 3 wire 100 ohm Platinum 0.0(C, α = 0.00385.

Reference Frick Technical Bulletin E70-020 TB for an explanation of vibration units and setpoints.
	Control
	Description
	Value
	Default
	Range
	Units

	Compressor Vibration -Suction


	Current value
	
	
	0-30
	gF

	
	Offset
	     
	0.0
	-3 to +3
	

	
	Sensor Signal
	 FORMDROPDOWN 

	Vibration
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	17
	
	

	Compressor Vibration - Discharge


	Current value
	
	
	0-30
	gF

	
	Offset
	     
	0.0
	-3 to +3
	


	
	Sensor Signal
	 FORMDROPDOWN 

	Vibration
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	18
	
	

	Motor Vibration - Shaft Side
	Current value
	
	
	0-30
	gF

	
	Offset
	     
	0.0
	-3 to +3
	

	
	Sensor Signal
	 FORMDROPDOWN 

	Vibration
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	19
	
	

	Motor Vibration - Opposite Shaft Side
	Current value
	
	
	0-30
	gF

	
	Offset
	     
	0.0
	-3 to +3
	

	
	Sensor Signal
	 FORMDROPDOWN 

	Vibration
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	20
	
	

	Motor Bearing Shaft Side Temperature


	Current value
	
	
	32 - 500
	Temperature
	F

	
	Offset
	     
	0.0
	-92.3 to +92.3
	
	

	
	Sensor Signal
	 FORMDROPDOWN 

	RTD
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	19
	
	

	Motor Bearing Opposite Shaft Side Temperature 


	Current value
	
	
	32 - 500
	Temperature
	F

	
	Offset
	     
	0.0
	-92.3 to +92.3
	
	

	
	Sensor Signal
	 FORMDROPDOWN 

	RTD
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	I/O Channel
	     
	20
	
	

	Motor Stator #1


	Current value
	
	
	32 - 500(F
	Temperature
	F

	
	Offset
	     
	0.0
	-92.3 to +92.3
	
	

	
	Sensor Signal
	 FORMDROPDOWN 

	RTD
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	21
	
	

	Motor Stator #2


	Current value
	
	
	32 - 500(F
	Temperature
	F

	
	Offset
	     
	0.0
	-92.3 to +92.3
	
	

	
	Sensor Signal
	 FORMDROPDOWN 

	RTD
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	22
	
	

	Motor Stator #3


	Current value
	
	
	32 - 500(F
	Temperature
	F

	
	Offset
	     
	0.0
	-92.3 to +92.3
	
	

	
	Sensor Signal
	 FORMDROPDOWN 

	RTD
	None
	None

	
	IO Board *
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	23
	
	


CALIBRATION / ANALOG OUTPUTS / RETRANSMITTING OUTPUTS

	Output Channel
	Description
	Value
	Default
	Range
	Units

	A
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	
	

	
	Device Channel
	     
	3
	
	

	B
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	C
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	D
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	E
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	F
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	G
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	

	H
	Input Channel to Retransmit
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Capacity Slide Position
	None
	None

	
	Device Source *
	 FORMDROPDOWN 

	None
	
	

	
	Device Channel
	     
	0
	
	


The following are the type of selectable inputs that are available for the device source:

* Device Source

	None

	Analog Board 1

	Analog Board 2


ANALOG OUTPUTS / VFD CONDENSER ANALOG OUTPUTS

	Output Channel
	Description
	Value
	Default
	Range
	Units

	Compressor VFD
	Device Source *
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	Device Channel
	     
	3
	
	

	Condenser Output A
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	None
	None

	
	Device Channel
	     
	5
	
	

	Condenser Output B
	Device Source *
	 FORMDROPDOWN 

	Analog Board 1
	None
	None

	
	Device Channel
	     
	6
	
	


The following are the type of selectable inputs that are available for the device source:

* Device Source

	None

	Analog Board 1

	Analog Board 2


CALIBRATION / AUXILIARIES / PAGE 2
	Item #
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 1
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	5
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 2
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	6
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 3
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	7
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 4
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	8
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 5
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	9
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	


CALIBRATION / AUXILIARIES / PAGE 2 (Continued)
	Item #
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 6
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	5
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 7
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	6
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 8
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	7
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 9
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	8
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	Auxiliary Analog 10
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	9
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	

	EZ Cool Feedback %
	Device Source*
	 FORMDROPDOWN 

	Analog Board 2
	None
	None

	
	I/O Channel
	     
	9
	
	

	
	Sensor Signal *
	 FORMDROPDOWN 

	1-5 V
	
	

	
	Sensor Type **
	 FORMDROPDOWN 

	Pressure
	
	

	
	Units if Type is Other
	     
	None
	
	


CALIBRATION / AUXILIARIES / PAGE 1

	Item #
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 1
	Name
	     
	Auxiliary Analog 1
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 2
	Name
	     
	Auxiliary Analog 2
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 3
	Name
	     
	Auxiliary Analog 3
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 4
	Name
	     
	Auxiliary Analog 4
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 5
	Name
	     
	Auxiliary Analog 5
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 6
	Name
	     
	Auxiliary Analog 6
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 7
	Name
	     
	Auxiliary Analog 7
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 8
	Name
	     
	Auxiliary Analog 8
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	Auxiliary Analog 9
	Name
	     
	Auxiliary Analog 9
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG


CALIBRATION / AUXILIARIES / PAGE 1 (Continued)
	Item #
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 10
	Name
	     
	Auxiliary Analog 10
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	30.0
	0.0 to 1435.6
	PSIG

	
	
	High
	     
	485.3
	0.0 to 1435.6
	PSIG

	EZ Cool Feedback %
	Name
	     
	EZ Cool Feedback %
	None

	
	Current Value
	     
	None
	

	
	Offset
	     
	0.0
	

	
	Range
	Low
	     
	0.0
	0.0 to 100.0
	Percent

	
	
	High
	     
	100.0
	0.0 to 100.0
	Percent


The following are the type of selectable inputs that are available for the device source, and signal selections:

* Sensor Signal Selections:





** Sensor Type

	None
	4-20mA
	RTD
	Vibration
	
	None

	0-5V
	Pot.
	CT
	1-10V
	
	Pressure

	1-5V
	ICTD
	RPM
	+/- 5V
	
	Temperature

	
	
	
	
	
	Other


*Auxiliary Analog selectable minimum and maximum ranges and offsets values:
*Program will inform user if values are out of range.
	
	RANGE
	OFFSET

	
	MININUM
	MAXIMUM
	MININUM
	MAXIMUM

	PRESSURE
	30 Hg
	1435.6 PSIG
	-75 PSIG
	+75 PSIG

	TEMPERATURE
	-1768 (F
	+18032(F
	-620.5(F
	+620.5(F

	OTHER
	-1000
	+10000
	-50
	+50


EZ Cool Feedback is a fixed value.
SETPOINTS

SETPOINTS / CAPACITY CONTROL SETPOINTS / (MODE 1 )

(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	PRESSURE

REGULATION
	Capacity Control
	Setpoint
	     
	20.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 100.0
	Pressure

(Magnitude)
	PSIG

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	
	0.5
	0.0 to 2.9
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	3
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Pressure
	     
	25.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Pressure
	     
	15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	0.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	
	
	
	

	
	
	Warning
	Setpoint
	     
	
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	TIME
	SEC

	TEMPERATURE

REGULATION
	Capacity Control
	Setpoint
	     
	40.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 90.0
	Temperature (Magnitude)
	F

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	     
	1.0
	0.0 to 36.0
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	4
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Temp.
	     
	45.0
	-491.1 to 431.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Temp.
	     
	36.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	35.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Force Unload
	     
	34.0
	
	
	

	
	
	Warning
	Setpoint
	     
	33.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	32.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	3
	0 to60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	7.6
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC


 SETPOINTS / CAPACITY CONTROL SETPOINTS / (MODE 2)

(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units


	PRESSURE

REGULATION
	Capacity Control
	Setpoint
	     
	20.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 100.0
	Pressure

(Magnitude)
	PSIG

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	
	0.5
	0.0 to 2.9
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	3
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Pressure
	     
	25.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Pressure
	     
	15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	0.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	
	
	
	

	
	
	Warning
	Setpoint
	     
	
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	TIME
	SEC

	TEMPERATURE

REGULATION
	Capacity Control
	Setpoint
	     
	40.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 90.0
	Temperature (Magnitude)
	F

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	     
	1.0
	0.0 to 36.0
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	4
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Temp.
	     
	45.0
	-491.1 to 431.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Temp.
	     
	36.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	35.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Force Unload
	     
	34.0
	
	
	

	
	
	Warning
	Setpoint
	     
	33.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	32.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	3
	0 to60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	7.6
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC


SETPOINTS / CAPACITY CONTROL SETPOINTS / (MODE 3)

(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	PRESSURE

REGULATION
	Capacity Control
	Setpoint
	     
	20.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 100.0
	Pressure

(Magnitude)
	PSIG

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	
	0.5
	0.0 to 2.9
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	3
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Pressure
	     
	25.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Pressure
	     
	15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	0.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	
	
	
	

	
	
	Warning
	Setpoint
	     
	
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	TIME
	SEC

	TEMPERATURE

REGULATION
	Capacity Control
	Setpoint
	     
	40.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 90.0
	Temperature (Magnitude)
	F

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	     
	1.0
	0.0 to 36.0
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	4
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Temp.
	     
	45.0
	-491.1 to 431.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Temp.
	     
	36.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	35.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Force Unload
	     
	34.0
	
	
	

	
	
	Warning
	Setpoint
	     
	33.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	32.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	3
	0 to60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	7.6
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC


SETPOINTS / CAPACITY CONTROL SETPOINTS / (MODE 4)

(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	PRESSURE

REGULATION
	Capacity Control
	Setpoint
	     
	20.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 100.0
	Pressure

(Magnitude)
	PSIG

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	
	0.5
	0.0 to 2.9
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	3
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Pressure
	     
	25.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Pressure
	     
	15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	0.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	
	
	
	

	
	
	Warning
	Setpoint
	     
	
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	-15.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	TIME
	SEC

	TEMPERATURE

REGULATION
	Capacity Control
	Setpoint
	     
	40.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Proportional Band
	High
	     
	15.0
	0.0 to 90.0
	Temperature (Magnitude)
	F

	
	
	
	Low
	     
	
	
	
	

	
	
	Dead Band 
	High
	     
	1.0
	0.0 to 36.0
	
	

	
	
	
	Low
	     
	
	
	
	

	
	
	Cycle Time 
	High
	     
	4
	0 to 60
	Time
	SEC

	
	
	
	Low
	     
	
	
	
	

	
	Autocycle
	Start
	Temp.
	     
	45.0
	-491.1 to 431.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to 60
	Time
	MIN

	
	
	Stop
	Temp.
	     
	36.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	1
	0 to60
	Time
	MIN

	
	Regulation Safeties
	Load Inhibit
	     
	35.0
	-459.4 to 463.1
	Temperature
	F

	
	
	Force Unload
	     
	34.0
	
	
	

	
	
	Warning
	Setpoint
	     
	33.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	32.0
	-459.4 to 463.1
	Temperature
	F

	
	
	
	Delay
	     
	3
	0 to60
	Time
	SEC

	
	Low Suction
	Load Inhibit
	     
	10.0
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Force Unload
	     
	5.0
	
	
	

	
	
	Warning
	Setpoint
	     
	2.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	7.6
	0.0 to 200.0
	Pressure
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC


SETPOINTS / SEQUENCING / SYSTEM 1 SETUP
Note:  Sequencing screen will only be shown when sequencing is enabled in the compressor configuration screen.
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	System 1 Setup
	Sequencing
	 FORMDROPDOWN 

	Disabled
	Disabled / Enabled
	None

	
	Setpoint
	     
	32.0
	0.0 to 185.3
	Temp.
	F

	
	Minimum Run Time
	     
	20
	0 to 300
	Time
	MIN

	
	High Stage System Link
	 FORMDROPDOWN 

	None
	None / System 2 / System 3
	None

	1
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	2
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	3
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	4
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	5
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	6
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	7
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	8
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / SEQUENCING / SYSTEM 2 SETUP
Note:  Sequencing screen will only be shown when sequencing is enabled in the compressor configuration screen.
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	System 2 Setup
	Sequencing
	 FORMDROPDOWN 

	Disabled
	Disabled / Enabled
	None

	
	Setpoint
	     
	32.0
	0.0 to 185.3
	Temp.
	F

	
	Minimum Run Time
	     
	20
	0 to 300
	Time
	MIN

	
	High Stage System Link
	 FORMDROPDOWN 

	None
	None / System 1 / System 3
	None

	1
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	2
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	3
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	4
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	5
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	6
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	7
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	8
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / SEQUENCING / SYSTEM 3 SETUP
Note:  Sequencing screen will only be shown when sequencing is enabled in the compressor configuration screen.
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	System 3 Setup
	Sequencing
	 FORMDROPDOWN 

	Disabled
	Disabled / Enabled
	None

	
	Setpoint
	     
	32.0
	0.0 to 185.3
	Temp.
	F

	
	Minimum Run Time
	     
	20
	0 to 300
	Time
	MIN

	
	High Stage System Link
	 FORMDROPDOWN 

	None
	None / System 1 / System 2
	None

	1
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	2
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	3
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	4
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	5
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	6
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	7
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	

	8
	Sequencing ID
	     
	0
	0 to 255
	None

	
	Start
	     
	1
	1 to 8
	

	
	Compressor Mode
	 FORMDROPDOWN 

	Manual
	None
	

	
	Capacity Mode
	 FORMDROPDOWN 

	Manual
	0 to 100
	Percent
	%

	
	Minimum Capacity
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / SEQUENCING / SEQUENCING CONTROL
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Description
	Value
	Default
	Range
	Units

	Average Capacity For Start
	     
	90.0
	0.0 to 100.0
	Percent
	%

	Full Load Capacity Position
	     
	98.0
	0.0 to 100.0
	
	

	Minimum Capacity Dead Band
	     
	1.0
	0.0 to 20.0
	
	

	Start Failure Reset Delay
	     
	12.0
	0.0 to 600.0
	Time
	MIN

	Slide Valve Failure Safety
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	Enabled
	


SETPOINTS / COMPRESSOR SAFETIES
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	High Discharge

Temperature
	Load Inhibit
	     
	212.0
	32.0 to 250.0
	Temperature
	F

	
	Force Unload
	     
	
	
	
	

	
	Warning
	Setpoint
	     
	205.0
	
	
	

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	212.0
	32.0 to 250.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	Misc.
	Starting Diff. Press. Below
	     
	50.0
	0.0 to 380.0
	Pressure
	PSIG

	
	Dual Mode
	 FORMDROPDOWN 

	Disabled
	
	None
	None

	High Discharge

 Pressure
	Load Inhibit
	     
	190.0
	0.0 to 270.0
	Pressure
	PSIG

	
	Force Unload
	     
	200.0
	
	
	

	
	Warning
	Setpoint
	     
	220.0
	
	
	

	
	
	Delay
	     
	2
	0 to 5
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	270.0
	0.0 to 270.0
	Pressure
	PSIG

	
	
	Delay
	     
	2
	0 to 5
	Time
	SEC

	Misc.
	Highest Cap. To Permit Starting
	     
	10
	0 to 100
	Percent
	%

	
	Starting Period Before Permitting Cap. Increase
	     
	0
	0 to 999
	Time
	SEC

	
	Stopping Period for Capacity Unload
	     
	30
	0 to 300
	
	

	
	Compressor Automatic Mode Min. Capacity
	     
	10
	0 to 100
	Percent
	%

	
	Capacity Unload Assist
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	Separator Velocity Reference
	     
	0
	0 to 100
	

	
	Compression Ratio
	     
	4
	1 to 30
	

	
	Liquid Slugging
	Warning
	     
	10.0
	0.0 to 90.0
	Temperature
	F

	
	
	Shutdown
	     
	20.0
	
	
	

	High Suction Pressure
	Load Inhibit
	     
	105.3
	0.0 to 200.0
	Pressure
	PSIG

	
	Force Unload
	     
	115.3
	
	
	

	
	Warning
	Setpoint
	     
	125.3
	
	
	

	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	135.3
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Delay
	     
	2
	0 to 60
	Time
	SEC

	Economizer
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	On when above
	     
	90.0
	0 to 100
	Percent
	%

	
	Off when below
	     
	85.0
	
	
	

	
	Override: Discharge Press. < (suction x 1.6^k)
	     
	15.0
	0.0 to 100.0
	Pressure
	PSIG

	
	Port Value
	     
	1.6
	0.0 to 5.0
	None

	
	Pressure Input
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Fixed Pressure Setpoint
	     
	-6.0
	-14.70 to 185.3
	Pressure (Positive)
	PSIG

	Balance Piston
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	On
	     
	90
	0 to 100
	Percent
	%

	
	Off
	     
	85
	
	
	

	
	Ignore Delay
	     
	5
	0 to 60
	Time
	MIN

	
	Fail Delay
	     
	2
	
	
	

	Misc.
	Oil Log
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	
	Delay
	
	30
	0 to 300
	Time
	SEC

	
	Oil Pump Unload Assist
	 FORMDROPDOWN 

	Enabled
	None
	None

	
	Main Oil Injection
	On When Discharge Temp.
	Is Above
	     
	150.0
	32.0 to 212.0
	Temperature
	F

	
	
	
	For
	     
	5
	0 to 300
	Time
	SEC


SETPOINTS / PACKAGE SAFETIES
 (Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Low Oil Separator Temperature
	Warning
	Setpoint
	     
	55.0
	49.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	49.0
	49.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	Low Comp. Oil Temperature


	Warning
	Setpoint
	     
	55.0
	49.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	49.0
	49.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	High Comp. Oil Temperature
	Warning
	Setpoint
	     
	158.0
	100.0 to 230.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	167.0
	100.0 to 230.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	Low Comp. Oil Pressure
	Warning
	Setpoint
	     
	25.0
	0.0 to 45.0
	Pressure

(Differential)
	PSID

	
	
	Delay
	     
	600
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	30.0
	0.0 to 45.0
	Pressure

(Differential)
	PSID

	
	
	Delay
	     
	900
	0 to 60
	Time
	SEC

	High Filter Pressure
	Warning
	Setpoint
	     
	25.0
	0.0 to 344.8
	Pressure (Differential)
	PSID

	
	
	Delay
	     
	10
	0 to 60
	Time
	MIN

	
	Shutdown
	Setpoint
	     
	30.0
	0.0 to 344.8
	Pressure

(Differential)
	PSID

	
	
	Delay
	     
	15
	0 to 60
	Time
	MIN

	Main Oil Injection
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	Shutdown
	Setpoint
	     
	15.0
	5.0 to 50.0
	Pressure
	PSIG

	
	
	Delay
	     
	30
	0 to 60
	Time
	SEC

	Misc.
	Oil Heater Off Above
	     
	120.0
	100.0 to 150.0
	Temperature
	F

	
	High Level Shutdown Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Low Oil Level Delay
	     
	30
	0 to 30
	
	

	
	Oil Pump Lube Time Before Starting
	     
	0
	0 to 60
	
	

	
	Dual Pump Transition Time
	     
	10
	
	
	

	Pull Down
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	Capacity Position
	     
	5.0
	0.0 to 100.0
	Percent
	%

	
	Amount of Time
	     
	60
	0 to 900
	Time
	SEC

	Pump Down
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	On When Suction Above
	Setpoint
	     
	0.3
	0.0 to 200.0
	Pressure
	PSIG

	
	
	Delay
	     
	5
	0 to 60
	Time
	MIN

	DX Circuit
	#1 Action
	 FORMDROPDOWN 

	Disabled
	None
	None

	
	#2 Action
	 FORMDROPDOWN 

	
	
	

	
	DX Circuit 1 On When Above
	     
	90
	0.0 to 100.0
	Percent
	%

	
	DX Circuit 1 Off When Below
	     
	85
	0.0 to 100.0
	
	

	
	DX Circuit 2 On When Above
	     
	90
	0.0 to 100.0
	
	

	
	DX Circuit 2 Off When Below
	     
	85
	0.0 to 100.0
	
	


SETPOINTS / PACKAGE SAFETIES (Continued)
	Control
	Description
	Value
	Default
	Range
	Units

	Liquid Injection
	Enabled / Disabled
	 FORMDROPDOWN 

	Disabled
	
	

	
	On When Above
	Setpoint
	     
	122.0
	100.0 to 180.0
	Temperature
	F

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Dual Port Transition
	     
	4.2
	0.0 to 5.0
	None

	Misc.
	Hot Gas Bypass
	     
	0.0
	0.0 to 100%
	Percent
	%

	
	Power Assist
	     
	15
	0.0 to 60.0
	Time
	SEC.


SETPOINTS / DRIVE:  ELECTRIC MOTOR
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Name Plate
	Motor Amps
	     
	100.0
	0.0 to 3000.0
	Current
	AMPS

	
	Volts
	     
	480.0
	0.0 to 9999.0
	None

	
	Service Factor
	     
	1.15
	0.0 to 2.0
	

	
	Horse Power
	     
	100.0
	0.0 to 3000.0
	

	
	CT Factor
	     
	
	
	

	
	Recycle Delay
	     
	20
	20 to 255
	Time
	MIN

	High Motor Amps
	Load Inhibit
	     
	100.0
	0.0 to 3000.0
	Current
	AMPS

	
	Force Unload
	     
	105.0
	
	
	

	
	Warning
	Setpoint
	     
	110.0
	
	
	

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	
	Shutdown
	Setpoint
	     
	115.0
	0.0 to 3000.0
	Current
	AMPS

	
	
	Delay
	     
	5
	0 to 60
	Time
	SEC

	Low Motor Amps
	Shutdown
	Setpoint
	     
	25.0
	0.0 to 60.0
	Current
	AMPS

	
	
	Delay
	     
	30
	0 to 60
	Time
	SEC

	
	Confirmed Running Motor Amps
	     
	25.0
	0.0 to 750.0
	Current
	AMPS

	
	Starting Motor Amps Ignore Period
	     
	5
	0 to 30
	Time
	SEC

	Motor Starter

(See DBS Manual)
	Locked Rotor Current
	     
	0.0
	300.0 to 600.0
	Percent
	%

	
	Stall Time
	     
	0
	1 to 60
	Time
	SEC

	
	Jam Current Level
	     
	0.0
	100.0 to 600.0
	Percent
	%

	
	Jam Run Delay
	     
	0
	0.0 to 60
	Time
	SEC

	
	Service Factor
	     
	0.0
	75.0 to 125.0
	 Percent
	%

	
	Current Unbalance
	Warning Level
	     
	
	2.0 to 25.0
	
	

	
	
	Warning Delay
	     
	0
	0 to 240
	Time
	SEC

	
	RTD Temp.
	Warning Level
	     
	32.0
	32.0 to 500.0
	Temperature
	F

	
	
	Trip Level
	     
	
	
	
	


SETPOINTS / DRIVE:  ENGINE OR TURBINE
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Engine / Turbine
	Confirmed Running
	     
	450.0
	0.0 to 750.0
	Speed
	RPM

	
	Starting Maximum Delay
	     
	5
	0 to 60
	Time
	MIN

	
	Idle Speed
	     
	0.0
	0.0 to 100.0
	Percent
	%

	
	Cool Down Period Before Stopping
	     
	0
	0 to 999
	Time
	SEC

	
	High RPM
	Warning
	Setpoint
	     
	1900
	0 to 4000
	Speed
	RPM

	
	
	
	Delay
	     
	1
	0 to 5
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	2000
	0 to 4000
	Speed
	RPM

	
	
	
	Delay
	     
	1
	0 to 5
	Time
	SEC

	
	Low RPM
	Load Inhibit
	     
	1100
	0 to 3000
	Speed
	RPM

	
	
	Force Unload
	     
	1075
	
	
	

	
	
	Warning 
	Setpoint
	     
	700
	
	
	

	
	
	
	Delay
	     
	30
	0 to 180
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	600
	0 to 3000
	Speed
	RPM

	
	
	
	Delay
	     
	30
	0 to 180
	Time
	SEC

	Engine / Turbine / DBS
	Drive Output
	Maximum
	     
	100.0
	0 to 100.0
	Percent
	%

	
	
	Minimum
	     
	50.0
	
	
	

	
	Rate of Increase
	Setpoint
	     
	2.0
	0.1 to 25.0
	
	

	
	
	Delay
	     
	1
	0.0 to 30.0
	Time
	SEC

	
	Rate of Decrease
	Setpoint
	     
	2.0
	0.1 to 25.0
	Percent
	%

	
	
	Delay
	     
	1
	0.0 to 30.0
	Time
	SEC

	
	Drive will increase when SV loads to…
	     
	95.0
	0.0 to 100.0
	Percent
	%

	
	The drive will reach…
	     
	50.0
	
	
	

	
	Variable Speed Minimum SV Pos…
	     
	25.0
	
	
	

	Engine
	High Manifold Pressure
	Load Inhibit
	     
	-2.9
	0.0 to 45.7
	Pressure 
	PSIG

	
	
	Force Unload
	     
	-2.5
	
	
	

	
	
	Warning
	Setpoint 
	     
	-2.0
	
	
	

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC

	
	
	Shutdown
	Setpoint
	     
	-1.5
	0.0 to 45.7
	Pressure 
	PSIG

	
	
	
	Delay
	     
	3
	0 to 60
	Time
	SEC


SETPOINTS / DRIVE:  ENGINE OR TURBINE
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Skip Frequency Bands
	Bottom
	     
	0.0
	0.0 to 100.0
	Percent
	%

	
	Top
	     
	
	
	
	

	
	Bottom
	     
	
	
	
	

	
	Top
	     
	
	
	
	

	
	Bottom
	     
	
	
	
	

	
	Top
	     
	
	
	
	

	
	Bottom
	     
	
	
	
	

	
	Top
	     
	
	
	
	

	
	Bottom
	     
	
	
	
	

	
	Top
	     
	
	
	
	


SETPOINTS / CAPACITY POSITION

(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Capacity Position
	Maximum Capacity Position
	     
	100.0
	0.0 to 100.0
	Percent
	%

	
	Min Capacity Position for Non-VFD Types
	     
	0.0
	
	
	


SETPOINTS / CONDENSER / CONDENSER DIGITAL CONTROL
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Condenser Digital Control

	Condenser Control Setpoint
	     
	-14.7
	0.0 to 485.3
	Pressure
	PSIG

	
	Step #1
	     
	0
	0 to 4
	None

	
	Step #2
	     
	
	
	

	
	Step #3
	     
	
	
	

	
	Step #4
	     
	
	
	

	
	Step Up
	Deadband
	     
	0.0
	0.0 to 20.0
	Pressure 
	PSI

	
	
	Delay
	     
	0
	0 to 60
	Time
	SEC

	
	Step Down
	Deadband
	     
	0.0
	0.0 to 20.0
	Pressure
	PSI

	
	
	Delay
	     
	0
	0 to 60
	Time
	SEC

	
	High Pressure Override
	     
	200
	0.0 to 1000.0
	Pressure
	PSIG

	
	High Pressure Override Delay
	     
	5
	0.0 to 300.0
	Time
	SEC


SETPOINTS / CONDENSER / CONDENSER ANALOG CONTROL

(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Condenser Analog Control

	Condenser Control Setpoint
	     
	-14.7
	0.0 to 485.3
	Pressure
	PSIG

	
	Analog Output A 
	 FORMDROPDOWN 

	Disabled
	None

	
	Analog Output B
	 FORMDROPDOWN 

	Disabled
	

	
	Proportional Band
	     
	5.0
	0.0 to 100.0
	Pressure
	PSI

	
	Integration Time
	     
	30
	0.0 to 999.0
	Time
	SEC

	
	High Limit
	     
	100.0
	0.0 to 100.0
	Percent
	%

	
	Low Limit
	     
	40.0
	
	
	


SETPOINTS / MISCELLANEOUS
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Miscellaneous
	Remote Capacity Deadband
	     
	1.0
	0.5 to 20.0
	Percent
	%

	
	High Comp. Oil Pressure
	 FORMDROPDOWN 

	Disabled
	None

	
	High Comp Oil Pressure
	Shutdown
	     
	50.0
	0.0 to 500.0
	Pressure
	PSI

	
	
	Delay
	     
	5
	0.0 to 60.0
	Time
	SEC

	
	Max Slide Valve Timer
	     
	30
	0.0 to 600.0
	Time
	1/10 SEC

	
	Dewpoint Temp. Warning - Running
	 FORMDROPDOWN 

	Disabled
	None

	
	Dewpoint Temp. Warning - Running
	Safety Factor
	     
	20.0
	20.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 99.0
	Time
	MIN

	
	Dewpoint Temp. Warning – Off
	 FORMDROPDOWN 

	Disabled
	None

	
	Dewpoint Temp. Warning - Off
	Safety Factor
	     
	2.0
	0.0 to 100.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 99.0
	Time
	MIN

	
	
	Heater Control Safety Factor
	     
	5.0
	0.0 to 100.0
	Temperature
	F

	
	Maximum Discharge Pressure
	     
	270.0
	0.0 to 365.3
	Pressure 
	PSIG

	
	Maximum Discharge and Oil Temp.
	     
	250.0
	100.0 to 300.0
	Temperature
	F


SETPOINTS / SCHEDULING
	Scheduling
	 FORMDROPDOWN 


	Control
	Hour

(0-23)
	Min

(0-59)
	Mode 

(1-4)
	Hour

(0-23)
	Min

(0-59)
	Mode

(1-4)
	Hour

(0-23)
	Min

(0-59)
	Mode

(1-4)
	Hour

(0-23)
	Min

(0-59)
	Mode

(1-4)

	Sunday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Monday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Tuesday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Wednesday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Thursday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Friday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     

	Saturday
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     
	     


SETPOINTS / PHD Monitoring
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Compressor Bearing


	Compressor Bearing
	 FORMDROPDOWN 

	Disabled
	None

	
	Suction End
	High Warning
	     
	3.5
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	99
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	10.0
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	1
	0.0 to 999.0
	Time
	SEC

	
	Discharge End
	High Warning
	     
	3.5
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	99
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	10.0
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	1
	0.0 to 999.0
	Time
	SEC

	Motor Bearing
	Motor Bearing
	 FORMDROPDOWN 

	Disabled
	None

	
	Shaft Side
	High Warning
	     
	3.5
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	99
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	10.0
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	1
	0.0 to 999.0
	Time
	SEC

	
	Opposite Shaft
	High Warning
	     
	3.5
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	99
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	10.0
	0.0 to 30.0
	g’s F
	gF

	
	
	Delay
	     
	1
	0.0 to 999.0
	Time
	SEC

	
	Shaft Side
	High Warning
	     
	203.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	221.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	Opposite Shaft
	High Warning
	     
	203.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	221.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	Motor Stator
	Motor Stator
	 FORMDROPDOWN 

	Disabled
	None

	
	Stator #1
	High Warning
	     
	302.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	311.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	Stator #2
	High Warning
	     
	302.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	311.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	Stator #3
	High Warning
	     
	302.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC

	
	
	High Shutdown
	     
	311.0
	32.0 to 500.0
	Temperature
	F

	
	
	Delay
	     
	5
	0.0 to 999.0
	Time
	SEC


SETPOINTS / PID SETUP / PAGE 1
* Default, Range & Units will be based on the Control Point setting (settings shown are for the default Control Point setting of Capacity Slide).
	Control
	Description
	Value
	Default *
	Range *
	Units *

	PID 1
	Name
	  EZ Cool LIOC  
	PID 1
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	Analog 1
	
	

	
	Output Channel
	     
	1
	
	

	
	Setpoint
	     
	32.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	18.0
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 2
	Name
	     
	PID 2
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	Analog 1
	
	

	
	Output Channel
	     
	2
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	0
	0.0 to 1000.0
	

	
	Integration Time
	     
	30.0
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 3
	Name
	     
	PID 3
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	0
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 4
	Name
	     
	PID 4
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	0
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	0.0 to 1000.0
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	-50.0 to 150.0
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / PID SETUP / PAGE 2
* Default, Range & Units will be based on the Control Point setting (settings shown are for the default Control Point setting of Capacity Slide).

	Control
	Description
	Value
	Default *
	Range *
	Units *

	PID 5
	Name
	     
	PID 5
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	Analog 1
	
	

	
	Output Channel
	     
	1
	
	

	
	Setpoint
	     
	32.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	18.0
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 6
	Name
	     
	PID 6
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	Analog 1
	
	

	
	Output Channel
	     
	2
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	0
	0.0 to 1000.0
	

	
	Integration Time
	     
	30.0
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 7
	Name
	     
	PID 7
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	
	0
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	PID 8
	Name
	     
	PID 8
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Point
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Cap. slide
	
	

	
	IO Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	0
	
	

	
	Setpoint
	     
	0.0
	-1000.0 to 1000.0
	

	
	Prop. Band
	     
	
	0.0 to 1000.0
	

	
	Integration Time
	     
	30
	0.0 to 1000.0
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	-50.0 to 150.0
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / SUPERHEAT CONTROL SETUP
	Control
	Description
	Value
	Default *
	Range *
	Units *

	Superheat #1
	Name
	  Superheat #1  
	
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Pressure
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Suction 
	
	

	
	Control Temperature
	 FORMDROPDOWN 
 
	Discharge
	
	

	
	Output Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	1
	
	

	
	Setpoint
	     
	10.0
	-150.0 to 1000.0
	Temperature
	F

	
	Prop. Band
	     
	2.0
	0.0 to 100.0
	
	

	
	Integration Time
	     
	180
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	Superheat #2
	Name
	  Superheat #2  
	
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Pressure
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Suction 
	
	

	
	Control Temperature
	 FORMDROPDOWN 
 
	Discharge
	
	

	
	Output Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	1
	
	

	
	Setpoint
	     
	10.0
	-150.0 to 1000.0
	Temperature
	F

	
	Prop. Band
	     
	2.0
	0.0 to 1000.0
	
	

	
	Integration Time
	     
	180
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	

	Superheat #3
	Name
	  Superheat #3  
	
	Refer to S90-022 Operation
	None

	
	Control
	 FORMDROPDOWN 

	Disabled
	
	

	
	Action
	 FORMDROPDOWN 

	Forward
	
	

	
	Control Pressure
	 FORMDROPDOWN 
    FORMDROPDOWN 

	Suction 
	
	

	
	Control Temperature
	 FORMDROPDOWN 
 
	Discharge
	
	

	
	Output Board
	 FORMDROPDOWN 

	None
	
	

	
	Output Channel
	     
	1
	
	

	
	Setpoint
	     
	10.0
	-150.0 to 1000.0
	Temperature
	F

	
	Prop. Band
	     
	2.0
	0.0 to 1000.0
	
	

	
	Integration Time
	     
	180
	
	Time
	SEC

	
	High Limit
	     
	100.0
	-50.0 to 150.0
	Percent
	%

	
	Low Limit
	     
	0.0
	
	
	

	
	When Running Off Value
	     
	0.0
	0.0 to 100.0
	
	


SETPOINTS / PANEL
(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Panel
	Panel Heater 
	On
	     
	53.6
	32.0 to 77.0
	Temperature
	F

	
	
	Off
	     
	55.4
	
	
	

	
	Remote Enable Output
	 FORMDROPDOWN 

	Disabled
	None

	
	Input Module Capacity Mode Selection
	 FORMDROPDOWN 

	
	

	
	Permissive Start
	 FORMDROPDOWN 

	
	

	
	Power Fail Restart
	 FORMDROPDOWN 

	
	

	
	
	     
	0
	1.0 to 99.0
	Time
	MIN

	
	Run Hours
	
	0
	0.0 to 1 MIL
	
	HRS

	
	PLC Interlock
	 FORMDROPDOWN 

	Disabled
	None

	
	Remote Control Setpoint
	 FORMDROPDOWN 

	
	


SETPOINTS / AUXILIARIES / ANALOG INPUTS / PAGE 1

(Units will be based upon the settings of the Session Screen, defaults are shown here)

	Control
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 1
	Auxiliary Analog 1
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 2
	Auxiliary Analog 2
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 3
	Auxiliary Analog 3
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC


SETPOINTS / AUXILIARIES / ANALOG INPUTS / PAGE 1 (Continued)
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 4
	Auxiliary Analog 4
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 5
	Auxiliary Analog 5
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC


SETPOINTS / AUXILIARIES / ANALOG INPUTS / PAGE 2
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 6
	Auxiliary Analog 6
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 7
	Auxiliary Analog 7
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC


SETPOINTS / AUXILIARIES / ANALOG INPUTS / PAGE 2 (Continued)
(Units will be based upon the settings of the Session Screen, defaults are shown here)
	Control
	Description
	Value
	Default
	Range
	Units

	Auxiliary Analog 8
	Auxiliary Analog 8
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 9
	Auxiliary Analog 9
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	Auxiliary Analog 10
	Auxiliary Analog 10
	 FORMDROPDOWN 

	Disabled
	Disabled
	None

	
	
	
	
	Enabled
	

	
	Low Warning
	Setpoint
	
	-14.7
	-14.7 to 420.4
	Pressure 
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	Low Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Warning
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC

	
	High Shutdown
	Setpoint
	     
	-14.7
	-14.7 to 420.4
	Pressure
	PSIG

	
	
	Delay
	     
	0
	0 to 99
	Time
	SEC


 SETPOINTS / AUXILIARIES / DIGITAL INPUT CONFIGURATION
	Control
	Description
	Value
	Default
	Range
	Units

	Auxiliary Input 1
	Name***
	     
	Auxiliary Input 1
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 1
	
	

	
	IO Channel
	     
	17
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	     
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 2
	Name***
	
	Auxiliary Input 2
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 1
	
	

	
	IO Channel
	
	18
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 3
	Name***
	
	Auxiliary Input 3
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	9
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 4
	Name***
	
	Auxiliary Input 4
	None
	 one

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	20
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 5
	Name***
	
	Auxiliary Input 5
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	11
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 6
	Name***
	
	Auxiliary Input 6
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	12
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 7
	Name***
	
	Auxiliary Input 7
	None
	None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	13
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC

	Auxiliary Input 8
	Name***
	
	Auxiliary Input 8
	None
	 None

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	IO Channel
	
	14
	
	

	
	Activity
	 FORMDROPDOWN 

	Disabled
	
	

	
	Delay
	
	0
	0 to 60
	Time
	SEC


***Chinese version does not have option to change text for auxiliary input Name – default name only available.

 SETPOINTS / AUXILIARIES / DIGITAL OUTPUT CONFIGURATION
	Control
	Description
	Value
	Default
	Range
	Units

	Output 1
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	None

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	I/O Channel
	     
	7
	
	

	Output 2
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	I/O Channel
	     
	8
	
	

	Output 3
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	Dig. Bd. 2
	
	

	
	I/O Channel
	     
	18
	
	

	Output 4
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	Output 5
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	


SETPOINTS / AUXILIARIES / DIGITAL OUTPUT CONFIGURATION (Continued)
	Control
	Description
	Value
	Default
	Range
	Units

	Output 6
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	None

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	Output 7
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	Output 8
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	Output 9
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	

	Output 10
	Analog Channel
	 FORMDROPDOWN 
    FORMDROPDOWN 

	0
	0 to 100
	

	
	< >
	 FORMDROPDOWN 

	>
	< or >
	

	
	On When
	     
	0.0
	-10000.0 to 10000.0
	

	
	Off When
	     
	
	
	

	
	Control When
	 FORMDROPDOWN 

	Disabled
	None
	

	
	Device Source
	 FORMDROPDOWN 

	None
	
	

	
	I/O Channel
	     
	0
	
	


 Analog Inputs … 





 Digital Inputs





 Digital Outputs





 � HYPERLINK  \l "SEQUENCING_SYSTEM_1_SETUP_SCREEN" ��System 1 Setup





 System 2 Setup





 System 3 Setup�





 � HYPERLINK  \l "CALIBRATION_RETRANSMITTING_OUTPUTS" ��Condenser� Digital Control





 � HYPERLINK  \l "CALIBRATION_ANALOG_OUTPUTS" ��Condenser� Analog Control





 � HYPERLINK  \l "CAPACITY_CONTROL_MODE_1_SCREEN" ��Mode 1





 Mode 2





 Mode 3





 Mode 4�





 � HYPERLINK  \l "TRENDING_SETUP" ��Trending Setup�





 � HYPERLINK  \l "REAL_TIME_TRENDING" ��Real Time Trending�





 � HYPERLINK  \l "HISTORY_TRENDING" ��History Trending�





 � HYPERLINK  \l "REAL_TIME_DATA_LOG" ��Real Time Data Log


�


 � HYPERLINK  \l "HISTORY_DATA_LOG" ��History Data Log�





 � HYPERLINK  \l "TRENDING_SETUP_BACK" ��Trending…�





 � HYPERLINK  \l "MAINTENANCE" ��Maintenance�





 � HYPERLINK  \l "EVENT_LOG_SCREEN" ��Event Log�





 � HYPERLINK  \l "VIBRATION" ��VSD� Energy Savings





 �HYPERLINK  \l "CURRENT_SAFETIES"��Current�





 � HYPERLINK  \l "SAFETY_HISTORY" ��History�





 � HYPERLINK  \l "SEQUENCING_1" ��Sequencing�  





 � HYPERLINK  \l "USER_DEFINED_OPERATING_STATUS" ��User Defined�  





�HYPERLINK  \l "HOME_SCREEN"��Home


�


� HYPERLINK  \l "SEQUENCING_BACK" ��Operating Values…�





� HYPERLINK  \l "MODE_SETUP" ��Modes


�


�HYPERLINK  \l "CURRENT_SAFETIES_BACK"��Safeties…�





�HYPERLINK  \l "TRENDING_MENU"��System Status…�





� HYPERLINK  \l "CAPACITY_CONTROL_BOX" ��Setpoints…�





� HYPERLINK  \l "CALIBRATION_1_SCREEN" ��Calibration� …





�HYPERLINK  \l "CONFIGURATION_COMPRESSOR_MENU"��Configuration…


�


� HYPERLINK  \l "SESSION_SCREEN" ��Session�





Service …





�HYPERLINK  \l "HELP_SCREEN"��Help


�


� HYPERLINK  \l "ABOUT_SCREEN" ��About


�





 � HYPERLINK  \l "MODE_1_BOX" ��Capacity…�





 � HYPERLINK  \l "SYSTEM_1_SETUP_BOX" ��Sequencing…�





 � HYPERLINK  \l "COMPRESSOR_SAFETIES" ��Compressor�





 � HYPERLINK  \l "PACKAGE_SCREEN" ��Package�





 � HYPERLINK  \l "DRIVE_SCREEN" ��Drive�





 Miscellaneous





 � HYPERLINK  \l "SCHEDULING_SCREEN" ��Scheduling�





 �HYPERLINK  \l "CONDENSER_SCREEN"��Condenser …


�


 PHD Monitoring





 � HYPERLINK  \l "PID_1_BACK" ��PID Setup …�





 � HYPERLINK  \l "COMMUNICATIONS_SCREEN" ��Communications�





 Auxiliaries …





 � HYPERLINK  \l "PANEL_SCREEN" ��Panel�





 � HYPERLINK  \l "CALIBRATION_PT_SCREEN" ��Pressure


�


 Temperature





 �HYPERLINK  \l "CAPACITY_VOLUME_SCREEN"��Capacity/Volume


�


 Motor/� HYPERLINK  \l "MISCELLEANEOUS_AUXILIARIES_SCREEN" ��Miscellaneous�





 PHD





 �HYPERLINK  \l "CALIBRATION_RETRANSMITTING_OUTPUTS_BACK"��Analog Outputs�…





 Auxiliaries …








� HYPERLINK  \l "CONFIGURATION_COMPRESSOR_SCREEN" ��Compressor�





Communications





Ethernet





� HYPERLINK  \l "CONFIGURATION_SECURITY_SCREEN" ��Security�





 � HYPERLINK  \l "DIGITAL_SCREEN" ��Digital


�


 �HYPERLINK  \l "ANALOG_SCREEN"��Analog


�


 � HYPERLINK  \l "COMMUNICATIONS_LOG_SCREEN" ��Communications Log�





 � HYPERLINK  \l "MOTOR_BUMP_SCREEN" ��Motor Bump


�


 DBS Fault History





 � HYPERLINK  \l "SOFTWARE_MAINTENANCE_SCREEN" ��Communications� Loop Back Test





 Diagnostics





 Software Maintenance





 � HYPERLINK  \l "PID_1_SCREEN" ��Page 1�





 Page 2





 � HYPERLINK  \l "PID_1_SCREEN" ��Page 1�





 Page 2





 � HYPERLINK  \l "CALIBRATION_RETRANSMITTING_OUTPUTS" ��Retransmitting Outputs�


 � HYPERLINK  \l "CALIBRATION_ANALOG_OUTPUTS" ��Output Calibration�





 � HYPERLINK  \l "CONFIGURATION_DIGITAL_IO" ��Page 1�





 Page 2





The above graphic represents the menu structure, or tree, of the Quantum™ LX� XE "Quantum™-LX" � screens. Use this tree when accessing the various screens. � XE "screen" �Please note that this screen list is complete, and that certain screens may not be available as shown here, depending upon the enabled options.








	[image: image3.jpg]


Original:
Buterbaugh
Revision:
 DOCPROPERTY "Category"  \* MERGEFORMAT 5

Apprd: 
DAK DOCPROPERTY "Manager"  \* MERGEFORMAT 
Rev Date:
5 September 2008

File: v:\engser\elegrp\electrical design workbook\forms\lx quantum setpoint sheet 6.61.doc
	REVISION RECORD:  Revised To Latest Software Release Ver. 6.61
	Page 1 / 43



[image: image4.jpg]


[image: image5.jpg]


[image: image6.jpg]


[image: image7.jpg]


[image: image8.jpg]


[image: image9.jpg]


[image: image10.jpg]


