	 PRIVATE 

	
	
	

	
	ENGINEERED SYSTEMS (ESG)
	STANDARD NO.
	C-51

	
	ENGINEERING STANDARD
	PAGE
	1 OF 41

	YORK
	
	DATE
	03-28-04

	INTERNATIONAL
	TERMINALS-WIRE
	SUPERSEDES
	07-10-03

	CORPORATION
	FOR ELECTRICAL CONDUCTORS
	ECN
	0703-3026

	
	AND TERMINAL HOUSINGS
	PREPARED BY
	L.N. Fair

	
	
	APPROVED BY
	B.A. Smith



     This standard, defining the requirements of materials to be furnished or

     services to be performed, is not subject to interpretation.

1.
SCOPE
1.1.
This standard covers solderless electrical wire terminals of the Slotted Spring Spade, Push-On, Ring Tongue, Pin and Socket types, terminal housings and inline and butt splices.

1.2.
Tooling and Inspection:  Tooling should be used as recommended by terminal manufacturer for the particular terminal being applied.  (Information received with tooling should be retained, filed and followed as it contains the pertinent data required for quality application of terminals.)  Inspection and certification of tooling and terminations should be conducted per information contained in AMP Inc. publication "Guidelines for User Certification of AMP Tooling HB5079 and Information Received with Tooling and Applicators".

2.
RELATED STANDARDS
2.1.
Terminals supplied under this standard shall conform to the following where applicable:

(a)
Underwriters Laboratories, Inc., Standard UL 486A

(b)
Military Standard MS25036 for the Pre-Insulated Terminals

(c)
Underwriters Laboratories, Inc., Standard UL 310

     Electrical Quick-Connect Terminals

(d)
CSA Standard C22.2 No 65; Wire Connectors

(e)
CSA Standard C22.2 No. 153; Quick-Connect Terminals

(f)
ESG Standard E-155: Equipment and Procedures for Dyeing

Electrical Connector Housings

3.
MATERIAL CHARACTERISTICS
3.1.
Terminals shall be suitable for use with insulated stranded copper wire, plain or tinned.

3.2.
The terminals shall be capable of being attached on the wire by crimping with special tools.

3.3.
All terminals shall be brass, phosphor bronze or copper and shall be tin or gold plated as specified.

3.4.
The various types of terminals and related housings covered under this standard are shown in the following paragraphs:

(a)
Slotted Spring Spades - Paragraph 3.5

(b)
Ring-tongue Terminals - Paragraph 3.6

[image: image6.png]


(c)
Push-On (Quick Connect) Terminal - Paragraph 3.7

(d)
Wire Splices, Paragraph 3.8

(e)
AMP Universal MATE-N-LOK Housings and Contacts –

 Paragraph 3.9

(f)
AMP Commercial MATE-N-LOK Housings and Contacts –

      Paragraph 3.10

3.4
(Continued)

(g)
AMP Mini-Universal MATE-N-LOK Housings and Contacts -

Paragraph 3.11

(h) AMP Mini-Universal MATE-N-LOK 2 Housings and Contacts - 

Paragraph 3.12

(i) AMP Micro MATE-N-LOK Housing and Contacts – Paragraph 3.13

(j)
Single Leaf .156 Wire to Board Receptacle Housings and Contacts - Paragraph 3.14

(k) 
MTA-156 IDC Connector - Closed end for 18 AWG wire - paragraph 3.15

(l) 
AMP Mark II Econoseal J Series Housings and Contacts -

Paragraph 3.16

(m)
Receptacles for Relay Sockets - Paragraph 3.17

3.5.
Slotted Spring Spade Terminals:

(a)
General characteristics of slotted spring spade terminals shall be as shown in Table 3.5(a).


TABLE 3.5(a)
Detail Characteristics and Reference Tables
[image: image7.png]AL




TABLE 3.5(b)
Insulated Spring Spade Terminals (AMP Plasti-Grip)

[image: image8.png]



[image: image9.wmf]Wire

Stud

Recom

.

Size

Size

Max.

Max.

Wire

Wire

AWG

No.

Hole

Width

Length

Washer

Insulation

Strip

No.

"H"

"W"

"L"

Radius

(

O.D.)

Length

± 

.005

± 

.008

"C"

Max.

AMP

York

2

5/16

0.328

0.711

2.063

0.578

.473 max.

.453 - .484

324112

025-28684-000

1/0

1/4

0.265

0.807

2.426

0.625

.580 max.

.735 - .859

324056

025-28683-000

Primary dimensions 

(  ) are American standard inches, metric millimeter dimensions are in

brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED

UNITS

Part Number*

* = Indicates heavy duty

terminals

All dimensions are for reference purposes

only.

Terminal Dimensions

(in.)


[image: image10.png]€Min.

b c
Washer Washer
Radius Radius
Masx- Max.

Lo





TABLE 3.5(c)

Non-Insulated Spring Spade Terminals (AMP Solistrand)

[image: image11.png]



3.6.
Ring-Tongue Terminals:

Tables 3.6(a) to 3.6(f) incl. give dimensions, part numbers and other information on Ring-Tongue Type Terminals.

TABLE 3.6(a)
Detail Characteristics and Reference Tables
[image: image12.png]i




TABLE 3.6(b)
[image: image13.png]


Insulated Ring-Tongue Terminals (AMP Plasti-Grip)
[image: image14.png]



	Wire

Size

AWG No.
	Stud

Size

No.
	Terminal Dimensions (in.)
	Recommend.

Wire

Strip

Length
	Part Number


	Term.

Supp.

	
	
	**

Hole

“H”
	+/- .008

Width

“W”
	Max.

Length

“L”
	Min.

Clear

“C”
	Max.

Washer

Radius
	Wire

Insul.

(O.D.)

Max.
	
	
	

	
	
	
	
	
	
	
	
	
	AMP
	York
	

	22 - 16
	6
	0.145
	0.218
	0.684
	0.156
	
	0.140
	.203 - .234
	1-34142-1
	025—07172-000
	T

	22 - 16
	6
	0.145
	0.312
	0.856
	0.281
	
	0.140
	.203 - .234
	2-34147-1
	025-30981-000
	T

	22 - 16
	8
	0.171
	0.312
	0.856
	0.281
	
	0.140
	.203 - .234
	2-34148-1
	025-30983-000
	T

	22 - 16
	10
	0.197
	0.281
	0.809
	0.250
	
	0.170
	.203 - .234
	2-35451-1
	025-10254-000
	T

	22 - 16
	1/4
	0.265
	0.469
	1.090
	0.437
	
	0.140
	.203 - .234
	2-34150-1
	025-18946-000
	T

	16 – 14
	6
	0.145
	0.343
	0.871
	0.281
	
	0.170
	.203 - .234
	2-34159-1
	025-10533-000
	T

	16 – 14
	8
	0.171
	0.343
	0.871
	0.281
	
	0.170
	.203 - .234
	2-34160-1
	025-10865-000
	T

	16 – 14
	10
	0.197
	0.343
	0.871
	0.281
	
	0.170
	.203 - .234
	2-34161-1
	025-11083-000
	T

	16 – 14
	10
	0.197
	0.343
	1.406
	0.281
	
	.200 (*)
	.203 - .234
	2-34823-1
	025-11936-000
	T

	16 – 14
	0.25
	0.265
	0.469
	1.090
	0.437
	
	0.170
	.203 - .234
	34162
	025-21101-000
	LP

	16 – 14
	0.25
	0.265
	0.469
	1.090
	0.437
	
	0.170
	.203 - .234
	2-34162-1
	025-30997-000
	T

	16 - 14
	0.3125
	0.328
	0.469
	1.090
	0.437
	
	0.170
	.203 - .234
	34163
	025-29904-000
	LP

	16 – 14

[1.5 – 2.5]
	5/16

[M8]
	0.328

[8.33]
	0.469

[11.91]
	1.090

[27.68]
	0.437

[11.09]
	
	0.170

[4.32]
	.203 - .234

[5.15 – 5.94]
	34163
	025-38127-000
	LP

	16 – 14
	0.375
	0.391
	0.531
	1.230
	0.546
	
	0.170
	.203 - .234
	34164
	025-29612-000
	LP

	16 – 14
	3/8*
	0.390
	0.750
	1.594
	0.625
	
	0.200
	.203 - .234
	34826
	025-32956-000
	LP

	16 – 14

[1.5 – 2.5]
	10

[M5]
	0.197

[5.00]
	0.343

[8.71]
	1.407

[26.57]
	0.281

[7.14]
	
	.200*

[5.08]
	.203 - .234

[5.15 – 5.94]
	2-34823-1
	025-34056-000
	T

	12 - 10
	6
	0.145
	0.281
	0.953
	0.219
	
	0.250
	.312 – .343
	2-34852-1
	025-32520-000
	T

	12 - 10
	8
	0.171
	0.375
	1.094
	0.302
	
	0.250
	.312 - .343
	2-34853-1
	025-08499-000
	T

	12 – 10

[4 – 6]
	8

[M4]
	0.171

[4.34]
	0.375

[9.52]
	1.098

[27.89]
	0.302

[7.67]
	
	0.250

[6.35]
	.312 - .343

[7.92 – 8.71]
	2-34853-1


	025-34091-000
	T

	12 - 10
	10
	0.197
	0.375
	1.083
	0.302
	
	0.250
	.312 – .343
	2-34854-1
	025-08477-000
	T

	12 - 10
	12, 14, 1/4
	0.265
	0.531
	1.327
	0.468
	
	0.250
	.312 – .343
	2-34855-1
	025-08787-000
	T

	12 - 10
	5/16
	0.328
	0.531
	1.327
	0.468
	
	0.250
	.312 – .343
	2-34856-1
	025-28972-000
	T

	12 - 10
	3/8
	0.390
	0.593
	1.421
	0.531
	
	0.230
	.312 – .343
	2-34173-1
	025-28973-000
	T

	12 - 10
	1/2
	0.515
	0.750
	1.594
	0.625
	
	0.250
	5/16
	2-34837-4
	025-33728-000
	T

	12 – 10

[4 – 6]
	1/2

[M12]
	0.515

[13.08]
	0.750

[19.05]
	1.594

[40.49]
	0.625

[15.88]
	
	0.250

[6.35]
	5/16

[7.93]
	2-34837-4
	025-34092-000
	T

	8
	3/8
	0.390
	0.587
	1.696
	
	0.500
	0.360
	.328 - .359
	52291-1
	025-30412-000
	LP

	8
	1/4
	0.265
	0.478
	1.600
	
	0.437
	0.330
	.328 - .359
	52041-3
	025-29935-000
	LP

	6
	3/8
	0.390
	0.625
	1.906
	
	0.515
	0.450
	.609 - .641
	52264-1
	025-30418-000
	LP

	6

[16]
	3/8

[M10]
	0.390

[9.91]
	0.625

[15.87]
	1.906

[48.41]
	
	0.515

[13.08]
	0.450

[11.43]
	.609 - .641

[15.46-16.28]
	52264-1
	025-38129-000
	LP

	6
	1/4
	0.265
	0.500
	1.869
	
	0.515
	0.360
	.609 - .641
	52042-3
	025-28943-000
	LP

	6
	10
	0.197
	0.500
	1.869
	
	0.515
	0.340
	.609 - .641
	52042-5
	025-30416-000
	LP

	4
	3/8
	0.390
	0.679
	2.014
	
	0.531
	0.450
	.609 - .641
	52266-4
	025-30415-000
	LP

	4

[25]
	3/8

[M10]
	0.390

[9.91]
	0.679

[17.24]
	2.014

[51.15]
	
	0.531

[13.48]
	0.450

[11.43]
	.609 - .641

[15.46-16.28]
	52266-4
	025-38130-000
	LP

	4
	1/4
	0.265
	0.546
	1.948
	
	0.531
	0.450
	.609 - .641
	52043-3
	025-28681-000
	LP

	4
	10
	0.197
	0.546
	1.948
	
	0.531
	0.450
	.609 - .641
	52043-2
	025-30414-000
	LP

	2
	3/8
	0.390
	0.711
	2.089
	
	0.578
	0.560
	.453 - .484
	52044-5
	025-30411-000
	LP

	2
	1/4
	0.265
	0.675
	2.071
	
	0.578
	0.560
	.453 - .484
	52267-1
	025-28682-000
	LP

	2
	5/16
	0.328
	0.711
	2.089
	
	0.578
	0.560
	.453 - .484
	52044-4
	025-29649-000
	LP

	1/0
	3/8
	0.390
	0.807
	2.447
	
	0.625
	0.665
	.735 - .859
	52045-5
	025-30413-000
	LP

	1/0
	5/16
	0.328
	0.807
	2.447
	
	0.625
	0.684
	.735 - .859
	52045-1
	025-28685-000
	LP


* = indicates heavy duty terminals               Terminal Supplied: T = Tape Mounted

** = “H” Hole Tolerance                                             LP = Loose Piece

Stud Size ( 1/4 = ( .005

Stud Size ( 1/4 = ( .003

All Dimensions are for reference purposes only.

Primary Dimensions are American standard inches, Metric millimeter dimensions are in brackets [].

Bold part Numbers are for globally designed units.

TABLE 3.6(c)
Insulated Ring-Tongue Terminals (AMP Pre-Insulated Diamond Grip - PIDG)
[image: image15.png]D



for Military Applications

[image: image16.png]ik
oYy /‘ W7
@% L HOLE-\ e »
E
o L
Ty \(8
STRAIGHT 90° AU 45°
ADAPTER-1 ADAPTER-2 ADAPTER-3 ADAPTER-4

™

t..
B

o|o|
- Wil

=625 —{

STRAIGHT

.250 FASTON

ADAPTER-5

wsﬁw
STl
W[

45°
.250 FASTON
ADAPTER-6

525 -t

k3434




   TABLE 3.6(d)
Insulated Ring-Tongue Terminals (AMP Terminal)
[image: image17.png]



[image: image18.png]..t
GD @D
l"—"L'—"I




TABLE 3.6(e)

Non-insulated Ring-Tongue Terminals (AMP Solistrand)

[image: image19.png]..t
GD @D
l"—"L'—"I




	Wire

Size

AWG No.
	Stud

Size

No.
	Style
	Terminal Dimensions (in.)
	Recommend.

Wire

Strip

Length
	Part Number


	Term.

Supp.

	
	
	
	Hole

“H”
	 Width

“W”
	Max.

Length

“L”
	Min.

Clear

“C”
	
	
	

	
	
	
	
	
	
	
	
	AMP
	York
	

	22 - 16
	10
	A
	0.197
	0.312
	0.621
	0.281
	1/4
	2-34112-2
	025—08803-000
	T

	16 - 14
	10
	A
	0.197
	0.343
	0.636
	0.281
	1/4
	2-34123-1
	025-11595-000
	T

	16 - 14
	12, 14, 1/4
	A
	0.265
	0.469
	0.855
	0.434
	1/4
	2-34124-1
	025-11164-000
	T

	16 - 14
	8
	A
	0.171
	0.343
	0.636
	0.281
	1/4
	2-34122-1
	025-04475-000
	T

	12 - 10
	6
	A
	0.145
	0.375
	0.765
	0.302
	5/16
	2-33456-1
	025-32551-000
	T

	12 - 10
	8
	A
	0.171
	0.375
	0.765
	0.302
	5/16
	2-32994-1
	025-12611-000
	T

	12 - 10
	10
	A
	0.197
	0.375
	0.765
	0.302
	5/16
	2-33457-2
	025-04474-000
	T

	12 - 10
	1/4
	A
	0.265
	0.531
	1.004
	0.468
	5/16
	2-33458-3
	
	T

	12 – 10

[4 – 6]
	1/4

[M6]
	A
	0.265

[16.73]
	0.531

[13.49]
	1.004

[25.50]
	0.468

[11.89]
	5/16

[7.94]
	2-33458-3
	025-33794-000
	T

	12 – 10

[4 – 6]
	7/16

[M11]
	A
	0.453

[11.51]
	
	
	
	5/16

[7.94]
	
	025-33787-000
	T

	12 – 10

[4 – 6]
	1/2

[M12]
	A
	0.515

[13.08]
	0.750

[19.05]
	1.271

[32.28]
	0.625

[15.88]
	5/16

[7.94]
	2-35135-2
	025-33789-000
	LP

	8
	10
	B
	0.197
	0.469
	0.933
	0.359
	11/32
	2-33460-2
	
	T

	8
	1/4
	B
	0.265
	0.469
	0.933
	0.359
	11/32
	2-33461-2
	025-04473-000
	T

	8

[10]
	1/4

[M6]
	B
	0.265

[6.73]
	0.469

[11.91]
	0.933

[23.70]
	0.359

[9.12]
	11/32

[8.73]
	2-33461-2
	025-33792-000
	T

	8
	3/8
	B
	0.390
	0.594
	1.168
	0.531
	11/32
	33463
	025-15143-000
	LP

	8

[10]
	3/8

[M10]
	B
	0.453

[11.51]
	0.594

[15.08]
	1.168

[29.66]
	0.531

[13.49]
	11/32

[8.73]
	33463
	025-38131-000
	LP

	8

[10]
	7/16

[M11]
	B
	0.453

[11.51]
	
	
	
	11/32

[8.73]
	
	025-33786-000
	LP

	8

[10]
	1/2

[M12]
	B
	0.515

[13.08]
	1.250

[31.75]
	1.965

[49.91]
	1.000

[25.40]
	11/32

[8.73]
	35664
	025-33788-000
	LP

	6

[16]
	1/4

[M6]
	B
	0.265

[6.73]
	0.625

[15.88]
	1.246

[31.65]
	0.531

[13.49]
	13/32

[10.32]
	2-33465-1
	025-33799-000
	T

	6
	7/16
	B
	0.453
	0.625
	1.246
	0.531
	13/32
	320745
	025-26298-000*
	LP

	6

[16]
	7/16

[M11]
	B
	0.453

[11.51]
	0.625

[15.88]
	1.246

[31.65]
	0.531

[13.49]
	13/32

[10.32]
	320745
	025-34039-000
	LP

	6

[16]
	1/2

[M12]
	B
	0.515

[13.08]
	0.875

[22.23]
	1.840

[46.74]
	1.000

[25.40]
	13/32

[10.32]
	320344
	025-34049-000
	LP

	4
	1/4
	B
	0.265
	0.500
	1.199
	0.437
	17/32
	31811
	025-25957-000
	LP

	4

[25]
	1/4

[M6]
	B
	0.265

[6.73]
	0.500

[12.70]
	1.199

[30.45]
	0.437

[11.10]
	17/32

[13.49]
	31811
	025-33791-000
	LP

	4
	7/16
	A
	0.453
	0.656
	1.314
	0.516
	17/32
	320743
	025-32934-000
	LP

	4

[25]
	7/16

[M11]
	A
	0.453

[11.51]
	0.656

[16.66]
	1.314

[33.38]
	0.516

[13.11]
	17/32

[13.49]
	320743
	025-34040-000
	LP

	4
	1/2
	B
	0.515
	0.875
	1.902
	1.000
	17/32
	327175
	025-25153-000
	LP

	4

[25]
	1/2

[M12]
	B
	0.515

[13.08]
	0.875

[22.23]
	1.902

[48.31]
	1.000

[25.40]
	17/32

[13.49]
	327175
	025-34050-000
	LP


* = Not recommended for new design               Terminal Supplied: T = Tape Mounted

                                                 LP = Loose Piece

All Dimensions are for reference purposes only.

Primary Dimensions are American standard inches, Metric millimeter dimensions are in brackets [].

Bold part Numbers are for globally designed units.

Continued on next page…

TABLE 3.6(e) (Cont’d.)

	Wire

Size

AWG

No.
	Stud

Size

No.
	Style
	
	Terminal
	Dimensions (in.)
	
	Recom.

Wire

Strip

Length
	Part Number
	Terminal

Supplied

	
	
	
	Hole

"H"
	Max.

Width

"W"
	Max.

Length

"L"
	Max.

Clear

"C"
	
	
	

	
	
	
	
	
	
	
	
	AMP
	York
	

	2
	1/4
	C
	0.265
	0.625
	1.527
	0.531
	17/32
	320383
	025-35939-000
	LP

	2

[35]
	1/4

[M6]
	C
	0.265

[6.73]
	0.625

[15.88]
	1.527

[38.79]
	0.531

[13.49]
	17/32

[13.49]
	320383
	025-37807-000
	LP

	2
	5/16
	D
	0.328
	0.890
	1.657
	0.531
	17/32
	35183
	025-35941-000
	LP

	2

[35]
	5/16

[M8]
	D
	0.328

[8.33]
	0.890

[22.61]
	1.657

[42.09]
	0.531

[13.49]
	17/32

[13.49]
	35183
	025-38128-000
	LP

	2
	3/8
	C
	0.390
	0.890
	1.657
	0.531
	17/32
	35184
	025-20913-000
	LP

	2
	7/16
	C
	0.453
	0.890
	1.657
	0.531
	17/32
	320741
	025-25152-000
	LP

	2

[35]
	7/16

[Mll]
	C
	0.453

[11.51]
	0.890

[22.61]
	1.657

[42.09]
	0.531

[13.49]
	17/32

[13.49]
	320741
	025-34041-000
	LP

	2

[35]
	3/8

[Ml0]
	C
	0.390

[9.91]
	0.890

[22.61]
	1.657

[42.09]
	0.531

[13.49]
	17/32

[13.49]
	35184
	025-34401-000
	LP

	2
	1/2
	C
	0.515
	0.890
	1.657
	0.531
	17/32
	35185
	025-34515-000
	LP

	2

[35]
	1/2

[M12]
	C
	0.515

[13.08]
	0.890

[22.61]
	1.657

[42.09]
	0.531

[13.49]
	17/32

[13.49]
	35185
	025-34051-000
	LP

	1

[50]
	1/2

[M12]
	C
	0.515

[13.08]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36919
	025-34052-000
	LP

	1

[50]
	7/16

[Mll]
	D
	0.453

[11.51]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36918
	025-34042-000
	LP

	1/0
	1/4
	D
	0.265
	0.875
	1.956
	0.625
	3/4
	36915
	025-25950-000
	LP

	1/0

[50]
	1/4

[M6]
	D
	0.265

[6.73]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36915
	025-37806-000
	LP

	1/0
	5/16
	D
	0.328
	0.875
	1.956
	0.625
	3/4
	36916
	025-20524-000
	LP

	1/0
	3/8
	D
	0.390
	0.875
	1.956
	0.625
	3/4
	36917
	025-20525-000
	LP

	1/0

[50]
	3/8

[Ml0]
	D
	0.390

[9.91]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36917
	025-37802-000
	LP

	1/0
	7/16
	D
	0.453
	0.875
	1.956
	0.625
	3/4
	36918
	025-25150-000
	LP

	1/0

[50]
	7/16

[Mll]
	D
	0.453

[11.51]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36918
	025-34043-000
	LP

	1/0
	1/2
	C
	0.515
	0.875
	1.956
	0.625
	3/4
	36919
	025-34514-000
	LP

	1/0

[50]
	1/2

[M12]
	C
	0.515

[13.08]
	0.875

[22.23]
	1.956

[49.68]
	0.625

[15.88]
	3/4

[19.05]
	36919
	025-33785-000
	LP

	2/0

[70]
	1/4

[M6]
	D
	0.265

[6.73]
	0.926

[23.52]
	1.930

[49.02]
	0.625

[15.88]
	3/4

[19.05]
	321869
	025-38530-000
	LP

	2/0
	5/16
	D
	0.328
	0.926
	1.930
	0.625
	3/4
	321870
	025-32946-000
	LP

	2/0
	3/8
	D
	0.390
	0.926
	1.930
	0.625
	3/4
	321871
	025-17710-000
	LP

	2/0

[70]
	3/8

[M10]
	D
	0.390

[9.91]
	0.926

[23.52]
	1.930

[49.02]
	0.625

[15.88]
	3/4

[19.05]
	321871
	025-37803-000
	LP

	2/0
	7/16
	D
	0.453
	0.926
	1.930
	0.625
	3/4
	321872
	025-25151-000
	LP

	2/0

[70]
	7/16

[M11]
	D
	0.453

[11.51]
	0.926

[23.52]
	1.930

[49.02]
	0.625

[15.88]
	3/4

[19.05]
	321872
	025-34044-000
	LP

	2/0
	1/2
	D
	0.515
	0.926
	1.930
	0.625
	3/4
	321873
	025-33729-000
	LP

	2/0

[70]
	1/2

[M12]
	D
	0.515

[13.08]
	0.926

[23.52]
	1.930

[49.02]
	0.625

[15.88]
	3/4

[19.05]
	321873
	025-34053-000
	LP

	2/0

[70]
	1/4

[M6]
	F
	.265

[6.73]
	.946

[24.03]
	1.930

[49.02]
	.432

[10.97]
	3/4

[19.05]
	324028
	025-387740-000
	LP

	2/0

[70]
	3/8

[M10]
	F
	.390

[9.91]
	.926

[23.52]
	1.687

[42.85]
	.531

[13.49]
	3/4

[19.05]
	322912
	025-38528-000
	LP

	2/0
	5/8
	F
	0.656
	1.270
	2.328
	1.000
	3/4
	696311-1
	025-35967-000
	LP

	3/0
	3/8
	D
	0.390
	1.020
	2.112
	0.625
	3/4
	321875
	025-31736-000
	LP

	3/0

[95]
	3/8

[Ml0]
	D
	0.390

[9.91]
	1.020

[25.91]
	2.112

[53.64]
	0.625

[15.88]
	3/4

[19.05]
	321875
	025-34459-000
	LP

	3/0
	7/16
	D
	0.453
	1.020
	2.112
	0.625
	3/4
	321876
	025-26296-000
	LP

	3/0

[95]
	7/16

[Mll]
	D
	0.453

[11.51]
	1.020

[25.91]
	2.112

[53.64]
	0.500

[12.70]
	3/4

[19.05]
	321876
	025-34045-000
	LP

	3/0
	1/2
	D
	0.515
	1.020
	2.112
	0.625
	3/4
	321877
	025-31737-000
	LP

	3/0

[95]
	1/2

[M12]
	D
	0.515

[13.08]
	1.020

[25.91]
	2.112

[53.64]
	0.500

[12.70]
	3/4

[19.05]
	321877
	025-34107-000
	LP

	3/0
	5/8
	F
	0.656
	1.270
	2.335
	0.925
	3/4
	696312-1
	025-35968-000
	LP

	* = Not Recommended for New Design                 Terminal Supplied T = Tape Mounted

                                                   LP = Loose Piece

All Dimensions are for reference purposes only.

Primary Dimensions are American standard inches, Metric millimeter dimensions are in brackets [].

Bold part Numbers are for globally designed units.


Continued on next page…

TABLE 3.6(e) (Cont’d.)

	Wire

Size

AWG

No.
	Stud

Size

No.
	Style
	
	Terminal
	Dimensions

(in.)
	
	Recom.

Wire

Strip

Length
	Part Number
	Terminal

Supplied

	
	
	
	Hole
	Max.
	Max.
	Max.
	
	AMP
	York
	

	
	
	
	“H”
	Width
	Length
	Clear
	
	
	
	

	
	
	
	
	“W”
	“L”
	“C”
	
	
	
	

	4/0
	1/4
	F
	0.265
	1.150
	1.864
	0.420
	49/64
	696393-1
	025-37851-000
	LP

	4/0
	5/16
	D
	0.328
	1.150
	2.537
	1.078
	49/64
	321271
	025-31738-000
	LP

	4/0
	5/16
	F
	0.328
	1.150
	2.194
	0.750
	49/64
	321272
	025-38141-000
	LP

	4/0
	3/8
	D
	0.390
	1.087
	2.178
	0.625
	49/64
	321878
	025-29626-000
	LP

	4/0

[107]
	3/8

[M10]
	D
	0.390

[9.91]
	1.087

[27.61]
	2.178

[55.32]
	0.625

[15.88]
	49/64

[19.45]
	321878
	025-34204-000
	LP

	4/0
	3/8
	E
	0.390
	1.115
	2.131
	0.681
	1-7/64
	321277-1
	025-34182-000
	LP

	4/0
	3/8
	F
	0.390
	1.140
	1.923
	0.484
	49/64
	321265
	025-38142-000
	LP

	4/0
	7/16
	D
	0.453
	1.087
	2.178
	0.625
	49/64
	321879
	025-26297-000
	LP

	4/0

[107]
	7/16

[Mll]
	D
	0.453

[11.51]
	1.087

[27.61]
	2.178

[55.32]
	0.625

[15.88]
	49/64

[19.45]
	321879
	025-34046-000
	LP

	4/0
	1/2
	D
	0.515
	1.087
	2.178
	0.625
	49/64
	321880
	025-29659-000
	LP

	4/0

[107]
	1/2

[M12]
	D
	0.515

[13.08]
	1.087

[27.61]
	2.178

[55.32]
	0.625

[15.88]
	49/64

[19.45]
	321880
	025-34200-000
	LP

	4/0
	5/8
	F
	0.656
	1.270
	2.444
	0.940
	49/64
	696313-1
	025-35969-000
	LP

	* = Not Recommended for New Design                        Terminal Supplied T = Tape Mounted

                                                                           LP = Loose Piece

All dimensions are for reference purposes only.

Primary dimensions ( ) are American standard inches, metric millimeter dimensions are in brackets [ ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


    TABLE 3.6(f)
Hole and Stud Sizes
[image: image20.png]



3.7
Push-On (Quick Connect) Terminals:

(a)
The Push-On Type Terminals are crimped onto stranded wire with special tools and then slipped over a flat male tab which is attached to the device being connected.

(1)
The matching male tab of all Push-On Type Terminals shall comply with Underwriters Laboratories Standard UL310.

(b)
The general characteristics of Push-on Type Terminals shall be as shown in Table 3.7(b).

TABLE 3.7(b)
[image: image21.png]



(c)
Tables 3.7(c) to 3.7(f) incl. and figures below, given dimensions, part numbers and detail information on the 

Push-On Type Terminals.

[image: image22.png]


[image: image23.png]


[image: image24.png]



         Straight Push-On             Straight Push-On

 

Flag Push-On

w/o Insulation Support
     w/ Insulation Support         w/ Insulation Support 
TABLE 3.7(c)
AMP Faston Series 250 Terminals - ESG Standard Types
[image: image25.png]




TABLE 3.7(d)

AMP Faston Series 250 Terminals - ESG Non-Standard Type
[image: image26.png]



TABLE 3.7(e)

AMP Faston Series 187 Terminals
	FITS .187” x .032” MALE TAB

	Type
	Wire
	Terminal Dimensions (in.)
	Recom.
	Part Number
	Remarks

	
	Size
	Width
	Width
	Length
	Wire*
	Wire
	
	

	
	AWG
	Inside
	Outside
	Overall
	Insulation
	Strip
	
	

	
	No.
	“T”
	“W”
	“L”
	(O.D.) *
	Length
	
	

	
	
	
	
	
	“D”
	
	AMP
	York
	

	Straight
	20 – 16
	0.040
	0.221
	0.470
	-----
	5/32
	42373-2
	025-08188-000
	

	Straight
	20 – 16
	0.040
	0.221
	0.470
	-----
	5/32
	42638-2
	025-25920-000
	Loose Piece

	[image: image27.png]


Straight
	18 – 14
	0.030
	0.225
	0.640
	.180 - .230
	7/32
	60742-2
	025-09455-000
	

	Flag
	18 – 14
	0.060
	0.230
	0.430
	.060 - .150
	3/16
	63512-1
	025-37821-000
	

	* = Wire insulation O.D. is given for those terminals having insulation support

All dimensions are for reference purposes only.

Primary dimensions (  ) are American standard inches, metric millimeter dimensions

are in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS




TABLE 3.7(f)

AMP Faston Insulated Series Terminals

[image: image28.png]



[image: image29.png]



                 Straight                                   Flag           

	FITS .250"  x  032"  MALE  TAB

	Type
	Wire

Size

AWG

No.


	Terminal Dimensions (in.)
	Recom.

Wire 

Strip

Length

(1) Wire 
	Recom.*
	Part  Number

	
	
	Thk.

"A"


	Width

"W"


	Length

"L"


	Wire*

Insulation

(O. D.) *

Max. "D"
	
	Wire
	

	
	
	
	
	
	
	
	Strip
	

	
	
	
	
	
	
	
	Length
	

	
	
	
	
	
	
	
	(2) Wires
	AMP
	MOLEX
	York

	Straight
	22 - 18
	0.195
	0.370
	0.855
	.135
	9/32
	5/16
	2-520183-2
	----
	025-21156-000

	Straight
	16 - 14
	0.195
	0.370
	0.935
	.260
	9/32
	5/16
	3-520140-2
	----
	025-23735-000

	Straight
	16- 14
	0.195
	0.409
	.935
	.160
	9/32
	5/16
	3-350820-2
	----
	025-35940-000

	Flag
	22 - 18
	0.187
	0.385
	0.636
	.165
	5/16
	.335
	2-520128-2
	----
	025-21771-000

	Flag
	16 - 14
	0.187
	0.385
	0.632
	.185
	5/16
	.335
	3-520132-2
	----
	025-23736-000

	Flag
	12-10
	0.196
	---
	.667
	.320
	9/32
	5/16
	----
	C-2211
	025-35976-000

	Straight
	12 - 10
	0.250
	0.373
	0.935
	0.320
	5/16
	5/16
	4-520447-2 
	----
	025-30996-000

	  * = Combination wire sizes may not exceed circular mil area of largest wire terminal will receive

  See reel/carbon labels for correct qtys.

  105 degree Max. operating temperature

  All dimensions are for reference purposes only.

  Primary dimensions (   ) are American standard inches, metric millimeter dimensions

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

	

	FITS .187" x .020"  MALE  TAB

	Type
	Wire
	Terminal 
	Dimensions (in.)
	Recom.
	Recom.*
	Part  Number

	
	Size
	Thk.
	Width
	Length
	Wire*
	Wire 
	Wire
	

	
	AWG
	"A"
	"W"
	"L"
	Insulation
	Strip
	Strip
	

	
	No.
	
	
	
	(O.D.) *
	Length
	Length
	

	
	
	
	
	
	Max. "D"
	(1) Wire
	(2) Wires
	AMP
	York

	Straight
	22 - 18
	0.165
	0.300
	0.855
	.135
	9/32
	5/16
	2-520181-2
	025-23737-000

	Straight
	16 - 14
	0.185
	0.300
	0.935
	.260
	9/32
	5/16
	3-520150-2
	025-23738-000

	Flag
	22 - 18
	0.187
	0.320
	0.636
	.165
	9/32
	5/16
	2-520334-2
	025-33774-000

	Flag
	16 - 14
	0.187
	0.320
	0.632
	.165
	9/32
	5/16
	3-520338-2
	025-33775-000

	  * = Combination wire sizes may not exceed circular mil area of largest wire terminal will receive

  See reel/carbon labels for correct qtys.

  105 degree Max. operating temperature

  All dimensions are for reference purposes only.

  Primary dimensions (   ) are American standard inches, metric millimeter dimensions

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


TABLE 3.7(f) (Cont’d.)

AMP Faston Insulated Series Terminals

	FITS  .110/125"  x  .020"  MALE  TAB

	Type
	Wire
	Terminal Dimensions (in.)
	Recom.
	Recom.*
	Part Number

	
	Size
	Thk.
	Width
	Length
	Wire*
	Wire 
	Wire
	

	
	AWG
	"A"
	"W"
	"L"
	Insulation
	Strip
	Strip
	

	
	No.
	
	
	
	(O.D.) *
	Length
	Length
	

	
	
	
	
	
	Max. "D"
	(1) Wire 
	(2) Wires
	AMP
	York

	Straight
	22 - 18
	0.081
	0.148
	0.734
	.100
	9/32
	N/A
	60894-1
	025-35935-000

	Straight
	22 - 18
	0.160
	0.239
	0.735
	.120
	9/32
	5/16
	2-520083-2
	025-32507-000

	Straight
	16 - 14
	0.175
	0.239
	0.865
	.260
	9/32
	5/16
	3-520370-2
	025-32840-000

	  * = Combination wire sizes may not exceed circular mil area of largest wire terminal will receive

  See reel/carbon labels for correct qtys.

  105 degree Max. operating temperature

  All dimensions are for reference purposes only.

  Primary dimensions (   ) are American standard inches, metric millimeter dimensions are in brackets [   ]

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

	
	

	
	

	
	

	
	

	
	

	MALE TAB TYPE   -    FITS .250" x .032"  FEMALE RECEPTACLE

	Type
	Wire
	Terminal Dimensions (in.)
	Recom.
	Recom.*
	Part Number

	
	Size
	Thk. 
	Width
	Length
	Wire*
	Wire 
	Wire
	

	
	AWG
	"A"
	"W"
	"L"
	Insulation
	Strip
	Strip
	

	
	No.
	
	
	
	(O.D.) *
	Length
	Length
	

	
	
	
	
	
	Max. "D"
	(1) Wire 
	(2) Wires
	AMP
	York

	Straight
	22 - 18
	0.290
	0.522
	0.855
	.135
	9/32
	5/16
	2-520102-2 
	025-32932-000

	Straight
	16 - 14
	0.290
	0.522
	0.855
	.160
	9/32
	5/16
	3-520106-2 
	025-31739-000

	  * = Combination wire sizes may not exceed circular mil area of largest wire terminal will receive

  See reel/carbon labels for correct qtys.

  105 degree Max. operating temperature

  All dimensions are for reference purposes only.1

  Primary dimensions (   ) are American standard inches, metric millimeter dimensions are in brackets [   ]

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


(g)
AMP Push-On Terminal Adapters are used to convert screw or rivet type terminals to Push-On Type, or to provide two connections when only one is available.  General characteristics shall be as shown in Table 3.7(g).


TABLE 3.7(g)

Push-On Terminal Adapters
[image: image30.png]2 and 3 Circuit,
In-Lifie

220
i e
. 833 110, IS
[2.37] 1279 _-‘ 163 183 -!__‘ 110 -—T;?gm—_-l
m =1 [414] 4.14]— | r_ [2.79]
B ]
fj — Y] [+9® |
n—= g e g
Plug Cap (Free Hanging)
4 and 6 Circuit, Dual Row
933 386 386 ; 933
l-—tza.701 — [' A~ 980 (o.80] A 23.70]
t
T" Co———T]
465 . T r,-; r‘—m'—“—fas
[11.81) N i N @ ¢ {11.81]
4 b e = I S i
.163 163 — e
(4.14] (4.14]
9, 12 and 15 Circuit.
Free Hanging
! 933 | A A 933
' [23.69) ] [23.69)

- | e = e ==
-630 g 9[- [13.99] [1"35919] . . 630
{16.0] ] @E [ B.l 116.00}

—] [@Qe 0] 1]
- .163 a8 ] ‘
[4.14] a4
Plug Cap
16 thru 24 Circuit,
Free Hanging, Dual Row
t
] .598
% {15.19]
4

l__ .933 ____,I

[23.70]




[image: image31.png]



3.8
Terminal Wire Splices are used to join conductors inside electrical closures.  Insulated butt splices are good for 600V applications.  Insulated closed end splices are good for 300V applications. Uninsulated parallel splices have voltage application dependent on the applied insulation.  Characteristics for insulated splices shall be as shown in Table 3.8(a), for uninsulated splices in Table 3.8(b).

TABLE 3.8(a)
Insulated Terminal Wire Splices

[image: image32.png]850t
{16.74}




[image: image33.png]679
[4.14) — = [17.25)
SPAC Max.
| 2
! 345 -
F——‘L [8.76)
| 950 l
i [24.13] !
Max

163
[4.14]

571

Max.

— 1

Cap

T [14.50)

571
[14.50
Max.





                     Butt Splice                       Closed End Splice
	AMP Butt and closed End

	Wire

Size

AWG No,
	Type
	Insulation

Color
	Max.

Length

“L”
	Wire

Insulation

(0.0,)

“0”
	Recom.

Wire

Strip

Length
	Part Number

	
	
	
	
	
	
	AMP
	York

	22 — 16
	Butt
	Red
	1.016
	.105 — .140
	1/4
	34070
	025 10535—000

	16 — 14
	Butt
	Blue
	1.065
	.115 — .170
	1/4
	34071
	025 13889 000

	22 - 16
	Closed End
	Blue
	0.750
	0.250
	11/32
	34349
	025 11093-000

	12 - 16
	Closed End
	Yellow
	1.010
	0.300
	7/16
	34865
	025 11095—000

	All dimensions are for reference purposes only.


Primary dimensions ( ) are American standard inches, metric millimeter


dimensions are in brackets 

BOLD PART NUNBER FOR GLOBALLY DESIGNED UNITS


TABLE 3.8(b)
Uninsulated Terminal Wire Splices

[image: image34.png]J75
(19.69) |




[image: image35.png]



Butt Splice                             Parallel Splice

	AMP Uninsulated Parallel Splices (Solistrand)

	Wire

Size

AWG No,
	Type
	Dim.

“L”
	Recom.

Wire

Strip 

Length
	Part Number

	
	
	
	
	AMP
	York

	22 -  16
	Parallel
	.301”
	
	34130
	

	16 -  14
	(
	.301”
	21/64
	34137
	025-37828-000

	12 - 10
	(
	.343”
	
	34138
	

	All dimensions are for reference purposes only.

Primary dimensions ( ) are American standard inches, metric millimeter

dimensions are in brackets 

BOLD PART NUNBER FOR GLOBALLY DESIGNED UNITS


	AMP Uninsulated Butt Splice (Solistrand)

	Wire
	Type
	Insulation
	Length
	Wire
	Recom.
	Part Number

	Size
	
	Color
	“L”
	Insulation
	Wire
	

	AWG No.
	
	
	
	(O.D.)
	Strip
	AMP
	York

	
	
	
	
	“D”
	Length
	
	

	16 -14
	Butt
	-----
	1.016
	-----
	1/4
	31819
	025-31752-0000

	All dimensions are for reference purposes only.

Primary dimensions ( ) are American standard inches, metric millimeter

dimensions are in brackets 

BOLD PART NUNBER FOR GLOBALLY DESIGNED UNITS


3.9
AMP Universal Mate-N-Lock housings and Universal Mate-N-Lock contacts are shown in Table 3.9(a) and Table 3.9(b) respectively.

TABLE 3.9(a)
Universal MATE-N-LOK Housings
[image: image36.png]


[image: image37.png]



                                                  3,4,5,6,8 and 10 Circuit.

             2 Circuit, In Line                      In Line (3 Shown)  

[image: image38.png]245

1622 |
100
[2.84)
7
A% 230
, [6.26) 15.84]
I Y
—d '\' L 050
725 [1.27)
{18.42)

097
(2.46]

'Mﬂ

156
(398"




[image: image39.png]i
(g

i
[




                6 Circuit                       9, 12 and 15 Circuit (9 Shown)

[image: image40.png]



TABLE 3.9(a) (Cont’d.)
[image: image41.png]



TABLE 3.9(b)
Universal MATE-N-LOK Contacts

[image: image1.png]



[image: image2.png]



                    Socket                       Pin

	Type (1)
	Wire

Size
	Wire Insulation

O.D.
	Recom.  Wire

Strip Length
	Part Number



	
	
	
	
	AMP 
	York

	
	
	
	
	
	

	
	
	
	
	
	

	 Pin
	20-14
	.130 - .200
	11/64
	350538-1
	 025-20533-000

	 Socket
	20-14
	.130 - .200
	11/64
	350537-1
	 025-19673-000

	 Socket
	20-14
	.060 - .130
	11/64
	350550-3
	 025-27232-000 **

	 Pin
	12-10
	.200 max. *
	11/64
	350922-3
	 025-20990-000 **

	 Socket
	12-10
	.200 max. *
	11/64
	350923-3
	 025-20991-000 **

	 Pin +
	20-14
	.130 - .200
	11/64
	350700-1
	 025-20919-000

	 Pin +
	20-14
	.060 - .130
	11/64
	350687-1
	 025-22214-000

	 Socket
	20-14
	.060 - .130
	11/64
	350536-1
	 025-22215-000

	*  - This contact has no insulation barrel, insulation maximum O.D. is 

       limited by housing.

**  - Contact is pre-tin plate phosphor bronze.

(1) - Pin and socket contacts can be used in either plug or cap universal

       MATE-N-LOK housings of Table 3.9(a).

All dimensions are for reference purposes only.

Primary dimensions ( ) are American standard inches, metric

millimeter dimensions are in brackets [ ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


3.10 
AMP Commercial MATE-N-LOK housings and Commercial MATE-N-LOK contacts are shown in table 3.10(a) and 3.10(b), respectively.

TABLE 3.10(a)

Commercial MATE-N-LOK Housings
[image: image42.png]


[image: image43.png]



  2 Circuit In-Line



   2 Circuit In-Line

           Pin Housing                               Socket Housing 
[image: image44.png]


[image: image45.png]



2,3 and 4 Circuit, Positive Lock          6,8,10,12 and 16 Circuit

          Socket Housing (3 Shown)              Socket Housing (6 Shown)
TABLE 3.10(a) (Cont’d.)

	Number

Of

Circuits
	Socket – Housing
	Pin - Housing

	
	Dim.

“A”
	Part Number
	Dim.

“A”
	Part Number

	
	
	AMP
	York
	
	AMP
	York

	2  (In-Line)
	.530
	1-480318-0**
	025-19667-000
	.610
	1-480319-0
	025-27974-000

	2
	.435
	1-480720-0
	025-21136-000
	
	
	

	2
	.435
	1-480720-2**
	025-27975-000
	
	
	

	3
	.630
	1-480721-0
	025-21137-000
	
	
	

	3
	.825
	1-480303-0
	025-37879-000
	.810
	1-480305-0
	025-34541-000

	4
	.830
	1-480722-0
	025-21138-000
	
	
	

	6
	.610
	1-480270-0
	025-19668-000
	
	
	

	8
	.805
	1-480283-0
	025-20972-000
	
	
	

	10
	1.000
	1-480285-0
	025-19514-000
	
	
	

	12
	1.195
	1-480287-0
	025-18955-000
	
	
	

	16
	1.585
	1-480438-0
	025-21139-000
	
	
	

	* = Material (Nylon 94V-2 Natural Color)

	** = Color Red (If not available order 025-21136-000 and dye red per E-155)

	All dimensions are for reference purposes only.

	Primary dimensions (  ) are American standard inches, metric millimeter

	dimensions are in brackets [  ]

	BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

	


TABLE3.10(b)

Commercial MATE-N-LOK Contacts

[image: image46.png]


[image: image47.png]AL




[image: image48.wmf]Dia. Hole

Dia. Hole

(H) +/-.003"

(H) +/-.005"

No.

Dia.

To Match

No.

Dia.

To Match

1

0.073

0.093

12

0.216

0.265

2

0.086

0.093

14

0.242

0.265

3

0.099

0.119

1/4

0.250

0.265

4

0.112

0.119

5/16

0.312

0.328

5

0.125

0.145

3/8

0.375

0.391

6

0.138

0.145

7/16

0.437

0.453

8

0.164

0.171

1/2

0.500

0.515

10

0.190

0.197

All dimensions are for reference purposes only.

Ring-Tongue Terminals

Stud Size

Stud Size


3.11
AMP Min-Universal MATE-N-LOK housings (plugs) and Mini-Universal MATE-N-LOK contacts (sockets) are shown in Table 3.11(a) and 3.11(b), respectively.

                                      TABLE 3.11(a)
[image: image49.wmf]AMP Faston

Matching

Reference

Item

Type

Series No.

Male Tab

Table No.

A

Straight

250

.250 x .032

3.7(c) & (d)

B

Flag (90 degree angle)

250

.250 x .032

3.7(c) & (d)

C

Straight

187

.187 x .020

3.7(e)

D

Adapters

250

.250 x .032

3.7(f)

All dimensions are for reference purposes only


TABLE 3.11(a) (Cont’d.)
	Number
	Dim. 
	Dim.
	Dim.
	Housing - Plug*
	Housing - Cap*

	of
	"A" 
	"B"
	"C"
	Part Number
	Part Number

	Circuits
	
	
	
	AMP
	York
	AMP
	York

	2
	.386
	.425
	.488
	172165-1
	025-29130-000
	172233-1
	025-32564-000

	3
	.551
	.591
	.654
	172166-1
	025-29185-000
	172234-1
	N/A

	4
	.386
	-----
	-----
	172167-1
	025-28959-000
	172159-1
	025-32962-000

	6
	.551
	-----
	-----
	172168-1
	025-28382-000
	172160-1
	025-32960-000

	9
	.551
	----
	----
	172169-1
	025-28383-000
	172161-1
	025-34537-000

	12
	.716
	----
	----
	172170-1
	025-28384-000
	172162-1
	025-34147-000

	15
	.882
	-----
	-----
	172171-1
	025-28385-000
	172163-1
	025-34539-000

	16
	1.366
	-----
	-----
	770583-1
	025-34143-000
	N/A
	N/A

	18
	1.529 
	-----
	-----
	770584-1
	025-35964-000
	N/A
	N/A

	20
	1.692
	-----
	-----
	770585-1
	025-34116-000
	N/A
	N/A

	22
	1.855
	-----
	-----
	770586-1
	025-34117-000
	N/A
	N/A

	24
	2.018
	-----
	-----
	770587-1
	025-34533-000
	N/A
	N/A

	  * = Material (Nylon 94V-0 White Color)

  All dimensions are for reference purposes only.

  Primary dimensions ( ) are American standard inches.

  Metric millimeter dimensions are in brackets [ ].

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


TABLE 3.11(b)
[image: image50.png]


Mini-Universal MATE-N-LOK Contacts
[image: image51.png]



     Pin                                Socket

	Contact
	Wire Size


	Wire Insulation O.D.
	Recom. Wire Strip Length
	Part Number

	
	
	
	
	Amp
	York

	Socket
	22 - 18
	.060 - .135
	1/8
	770904-1
	025-28686-000

	Pin
	22 –18
	.060 - .135
	1/8
	770903-1
	025-30999-000

	Socket, Gold
	20 x (2)
	.094 x (2)
	5/32
	171637-3
	025-39579-000

	Socket, Tin
	20 x (2)
	.094 x (2)
	5/32
	171637-1
	025-37830-000

	All dimensions are for reference purposes only.

Primary dimensions ( ) are American standard inches,

Metric millimeter dimensions are in brackets

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


3.12
AMP Min-Universal MATE-N-LOK 2 housings (plugs) and Mini-Universal MATE-N-LOK 2 contacts (sockets) are shown in Table 3.12(a) and 3.12(b), respectively.


TABLE 3.12(a)
[image: image52.png]i




[image: image53.png]D



          2 AND 3 CIRCUIT, IN-LINE

         4 AND 6 CIRCUIT, DUAL ROW

          9, 12 AND 15 CIRCUIT, MATRIX



8 and 16 thru 24 Circuit

[image: image54.png]




(Dual Row)

TABLE 3.12(a) (Cont’d.)

	Number
	Dim. 
	Dim.
	Dim.
	Housing - Plug*
	Housing - Cap*

	of
	"A" 
	"B"
	"C"
	Part Number
	Part Number

	Circuits
	
	
	
	AMP
	York
	AMP
	York

	2
	.405
	.679
	.571
	794184-1
	N/A
	794185-1
	N/A

	3
	.405
	.844
	.736
	794186-1
	N/A
	794187-1
	N/A

	4
	.571
	-----
	-----
	794188-1
	N/A
	794189-1
	N/A

	6
	.736
	-----
	-----
	794190-1
	N/A
	794191-1
	N/A

	8
	.899
	----
	----
	794192-1
	025-34144-000
	794193-1
	025-34557-000

	9
	.736
	----
	----
	794194-1
	N/A
	794195-1
	N/A

	12
	.901
	-----
	-----
	794200-1
	N/A
	794201-1
	N/A

	15
	1.067
	-----
	-----
	794204-1
	N/A
	794205-1
	N/A

	16
	1.551
	-----
	-----
	794206-1
	N/A
	794207-1
	025-37880-000

	18
	1.714
	-----
	-----
	794208-1
	N/A
	794209-1
	N/A

	20
	1.877
	-----
	-----
	794210-1
	N/A
	794211-1
	N/A

	22
	2.040
	-----
	-----
	794212-1
	N/A
	794213-1
	N/A

	24
	2.203
	-----
	-----
	794214-1
	N/A
	794215-1
	N/A

	  * = Material (Nylon 94V-0 White Color)

  All dimensions are for reference purposes only.

  Primary dimensions ( ) are American standard inches.

  Metric millimeter dimensions are in brackets [ ].

  BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


TABLE 3.12(b)
Mini-Universal MATE-N-LOK 2 Sockets
[image: image55.png]ik
oYy /‘ W7
@% L HOLE-\ e »
E
o L
Ty \(8
STRAIGHT 90° AU 45°
ADAPTER-1 ADAPTER-2 ADAPTER-3 ADAPTER-4

™

t..
B

o|o|
- Wil

=625 —{

STRAIGHT

.250 FASTON

ADAPTER-5

wsﬁw
STl
W[

45°
.250 FASTON
ADAPTER-6

525 -t

k3434



[image: image56.png]



Pin                           Socket

	Contact
	Wire
	Wire
	Recom.
	Part Number

	
	Size
	Insulation
	Wire
	

	
	
	O.D.
	Strip
	AMP
	York

	
	
	
	Length
	
	

	Socket
	20 – 16
	.079 - .126
	1/8
	794223-1
	025-34145-000

	Pin
	20 – 16
	.079 - .126
	1/8
	794222-1
	025-34563-000 

	All dimensions are for reference purposes only.

Primary dimensions (  ) are American standard inches,

Metric millimeter dimensions are in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS


3.13
AMP Micro MATE-N-LOK housings and Micro MATE-N-LOK contacts are shown in Table 3.13(a) and 3.13(b), respectively.

TABLE 3.13(a)

2 thru 24 CIRCUIT RECEPTACLE HOUSING DUAL ROW

[image: image3.png]18 TYP

a8

L pMAr20]

N
"\ Circuit 1 Identifier




2 thru 24 CIRCUIT PLUG HOUSING DUAL ROW
[image: image4.png]S Circuit 1 Wdentifier

e
Lha@nmmif'“ I E— =
r‘bn oflo]ee l
| omcae I
N






TABLE 3.13(a) (Cont’d)

	Number 
	Dim
	Housing – Receptacle*
	Dim
	Housing – Plug*

	Of 
	“A”
	Part number
	“A”
	Part number

	Circuits
	 
	AMP
	YORK
	 
	AMP
	YORK

	2
	0.157
	794617-2
	 
	0.157
	794616-2
	 

	4
	0.276
	794617-4
	 
	0.276
	794616-4
	 

	6
	0.394
	794617-6
	 
	0.94
	794616-6
	 

	8
	0.512
	794617-8
	025-39326-000
	0.512
	794616-8
	025-39334-000

	10
	0.63
	1-794617-0
	 
	0.63
	1-794616-0
	 

	12
	0.748
	1-794617-2
	025-39327-000
	0.748
	1-794616-2
	025-39335-000

	14
	0.866
	1-794617-4
	025-39328-000
	0.866
	1-794616-4
	025-39336-000

	16
	0.984
	1-794617-6
	 
	0.984
	1-794616-6
	 

	18
	1.102
	1-794617-8
	 
	1.102
	1-794616-8
	 

	20
	1.22
	2-794617-0
	 
	1.22
	2-794616-0
	 

	22
	1.339
	2-794617-2
	 
	1.339
	2-794616-2
	 

	24
	1.457
	2-794617-4
	 
	1.457
	2-794616-4
	 

	* = Material (Nylon 94V-0 Black Color)  

	All dimensions are for reference purposes only.

	Dimensions are American standard inches.


TABLE 3.13 (b)

[image: image5.png]



RECEPTACLE CONTACT



PLUG CONTACT

Table 3.13 (b) (Cont’d)

	Contact
	Wire
	Wire 
	Recom.
	Part Number

	 
	Size
	Insulation
	Wire
	 
	 

	 
	 
	O.D.
	Strip
	Amp
	York

	 
	 
	 
	Length
	 
	 

	Receptacle
	20-24
	.035 - .06
	 1/8
	794606-1
	025-39329-000

	Plug 
	20-24
	.035 - .06
	 1/8
	794608-1
	025-39333-000


3.14
Single Leaf .156 wire to board receptacle housings and contacts are shown in Table 3.14(a) and Table 3.14(b), respectively.


TABLE 3.14(a)

Housing with Locking RAMP


1 thru 24 Positions (3 Shown)
[image: image57.png]



[image: image58.png]..t
GD @D
l"—"L'—"I





TABLE 3.14(b)

Contacts - High Force
[image: image59.png]



[image: image60.png]



3.15
MTA-156 IDC Connector-Closed End for 18 AWG wire are shown in Table 3.15.


TABLE 3.15

Closed End with Locking RAMP


1 thru 24 Positions, 18 AWG

[image: image61.png]



[image: image62.png]



3.16
AMP Econoseal J Series waterproof Mark II housings and contacts are shown in Table 3.16(a) and Table 3.16(b), respectively.


TABLE 3.16(a)

Mark II Housings 2 and 3


Positions, In-Line (2 Shown)
[image: image63.png]


[image: image64.png]



      Cap (Tab) Housing                 Plug (Receptacle) Housing Assembly

[image: image65.png]




TABLE 3.16(b)

Mark II 070 Series Contacts and Rubber Collars

[image: image66.png]Max.

571
[14.50]

4

:_I»D]L
| B .
} iy
m =0 g3
o ¢
gy
!
4]
f
i o i 3
Jol] u_
(D)
3
N7
AN
{ AN
Y
tojlo] .
x
(eeesp <g
84N
NPy
A2 N I
BIrel 83
e =<
NS |
NN H
olfo
ENIES
nowﬁQHf
i1 e 1
by
o <
© -
~ s

Cap




       Tab *


   Receptacle *
       Rubber Collar **
[image: image67.png]



TABLE 3.17
AMP Crimp Type Receptacles*
[image: image68.png]



[image: image69.wmf]Type

Wire

Wire

Recom.

Size

Insulation

Wire

O.D.

Strip

York

Length

Loose

Reel

Pin

20 - 14

.130 max.

5/32

61118-1

-----

025-18443-000

Socket

20 - 14

.130 max.

5/32

61117-1

-----

025-19674-000

Socket

(2) 18

.115 max.

5/32

350557-1

-----

025-32506-000

Socket

24 - 18

.130 max.

5/32

60617-1

61314-4

025-33701-000

Primary dimensions (  ) are American standard inches, metric 

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

Part Number



AMP

millimeter dimensions are in brackets [  ]

All dimensions are for reference purposes only.


4.
INSPECTION
4.1
At its option, ESG may Inspect incoming shipments for compliance with this standard.  However, the supplier is responsible for full conformance with this standard without dependence on ESG inspection.

5.
APPROVED SOURCES OF SUPPLY
(a)
AMP Incorporated

(b)
Kent Division, The Thomas & Betts Co., for Terminal Adapters only

(c)
Kulka Smith, Inc., for Terminal Adapters only.

(d)
Marco Manufacturing, for Terminal Adapters only.

6.
PURCHASING
6.1
ESG Purchase Order shall specify:

(a)
Quantity

(b)
Type and Size

(c)
Manufacturer's name and part number

(d)
ESG Part Number

(e)
ESG Standard C-51

7.
APPLICATION (ENGINEERED SYSTEMS INFORMATION ONLY)
7.1
(a)
For factory wiring of refrigeration, air conditioning, heating equipment, and control panels.

(b)
The Ampere rating of the terminal shall be the same as that of the copper conductor AWG size being used.

(c)
Where insulated terminals must be used to meet Underwriter's spacing requirements, designer must refer to vendor catalog for voltage rating.

7.2
Slotted Spring Spade Terminals:

(a)
Use the Plasti-Grip Slotted Spring Spade terminal, of Table 3.5(b) as the preferred standard.

7.3
The Solistrand Slotted Spring Spade Terminal Table 3.5(c) is for general use where insulation is not required.  These terminals may be used with either stranded or solid wire.  For No. 12 AWG and larger sizes, UL approval covers stranded wire only.

7.4
Ring-Tongue Type Terminals:

(a)
Plasti-Grip Ring-Tongue Terminals of Table 3.6(b) are recommended for non-military designs.

(b)
The Diamond Grip (PIDG) Ring-Tongue Terminals of Table 3.6(c) is more costly and shall be used only when required for Military Equipment.

(c)
The Terminal Ring-Tongue Terminal of Table 3.6(d) shall be used for large wire sizes.  Where space is limited, the Solistrand Terminal of Table 3.6(e) may be used.  Insulating Tubing shall be used over the Solistrand Terminal where required to meet Underwriter's Laboratories electrical spacing.

(d)
The Solistrand Ring-Tongue Terminal of Tables 3.6(e) is for general use where insulation is not required.  These terminals may be used with either stranded or solid wire.  For No. 12 AWG and larger sizes, UL approval covers stranded wire only.

7.5
Push-On Type Terminals:

(a)
This type terminal permits much faster wiring on the equipment when the control device can be obtained with the matching male tab.  They are limited, however, to the wire sizes listed in Table 3.7(c).

(b)
These terminals are supplied in reels for Automatic Machine Operation, except where the Table shows "loose piece" only.

(c)
Most small compressors are fitted with 1/4" x .032" male tabs. For this application, the gap dimensions of the terminal are increased from .060" and .065" to .115" and .120" respectively, to provide for the stud to which the tab is welded.

(d)
Insulation, if necessary, may be applied to the inside of the connection box, or an insulating sleeve heat shrunk over the applied terminal.  The push-on terminals can be obtained in the pre-insulated form [See Table 3.7(f)]; however, different tooling is required.

(e)
Shop experience with .250" Push-On terminals has shown that a satisfactory grip can be made on the wire insulation even when the wire insulation diameter exceeds the recommended range by up to 50%.

7.5
Terminal Adapters, Push-On Type:

(a)
Table 3.7(g) shows push-on terminal adapters that are available.

(b)
The Dual Adapters, are used where two (2) male tabs are needed but only a single one is available.  The electrical clearance must not be reduced below the allowed minimum.

(c)
The male tab shall be used to convert a screw terminal to a Push-On Type.

7.6
Terminal Wire Splices:

(a)
Table 3.8 shows the Butt and Closed End Type Splices.

(b)
These splices are used inside the electrical enclosures for joining conductors up to 300 volt AC rating.  They shall not be used between enclosures or inside conduit.

(c)
Other splice connectors are available, see ESG Standard 

C-63.

7.7
General:

(a)
Insulated terminals are required when it is possible to turn them on a stud or screw to a position where the required electrical spacing is reduced below that specified in the applicable Underwriters' Laboratories Standard.

(b)
Insulated terminals are made to be crimped over the insulation of the wire.  The O.D. of the wire must therefore not exceed the I.D. of the insulation on the terminals.

(c)
The color code on Table 7.7(c) insures proper application of the terminals.  The symbol (Sym.) shown indicates the proper tool for each type and size.  Table 7.7(c) shows the proper tool marking on the applied terminal.  If the tool marks do not agree with this data, the wrong tool has been used and the terminal may not be tight.  A properly made terminal Joint will pass a pull test equal to 70-100% of the tensile strength of the wire.

   TABLE 7.7(c)
[image: image70.png]2 and 3 Circuit,
In-Lifie

220
i e
. 833 110, IS
[2.37] 1279 _-‘ 163 183 -!__‘ 110 -—T;?gm—_-l
m =1 [414] 4.14]— | r_ [2.79]
B ]
fj — Y] [+9® |
n—= g e g
Plug Cap (Free Hanging)
4 and 6 Circuit, Dual Row
933 386 386 ; 933
l-—tza.701 — [' A~ 980 (o.80] A 23.70]
t
T" Co———T]
465 . T r,-; r‘—m'—“—fas
[11.81) N i N @ ¢ {11.81]
4 b e = I S i
.163 163 — e
(4.14] (4.14]
9, 12 and 15 Circuit.
Free Hanging
! 933 | A A 933
' [23.69) ] [23.69)

- | e = e ==
-630 g 9[- [13.99] [1"35919] . . 630
{16.0] ] @E [ B.l 116.00}

—] [@Qe 0] 1]
- .163 a8 ] ‘
[4.14] a4
Plug Cap
16 thru 24 Circuit,
Free Hanging, Dual Row
t
] .598
% {15.19]
4

l__ .933 ____,I

[23.70]




7.8
Terminals with Multiple Wires:

(a)
The AWG wire range of Table 3.8 is for a single conductor for a Butt Splice and Two (2) conductors for a Closed End Splice.

(b)
If additional wires are required, the terminal AWG size must be calculated.  See paragraph 7.8(c).

(c) Using Table 7.8(c1), add the CMA (Circular Mill Area) values of the required wires and select from Tabled 7.8(C2) the proper AWG Terminal Connector based on the total CMA value.

TABLE 7.8(c1)

[image: image71.png]850t
{16.74}





TABLE 7.8 (c2)

[image: image72.png]679
[4.14) — = [17.25)
SPAC Max.
| 2
! 345 -
F——‘L [8.76)
| 950 l
i [24.13] !
Max

163
[4.14]

571

Max.

— 1

Cap

T [14.50)

571
[14.50
Max.





7.8
(Continued)

(e) Based on CMA and insulation thickness the following terminals should be used for multi-wire applications requiring Series 250 terminals:

     TABLE 7.8 (c3)

[image: image73.png]J75
(19.69) |





MOD IV WIRE - APPLIED HOUSINGS

SINGLE ROW  .100 CENTERS

[image: image74.png]



	 No.
	Diam.
	Housing Cap

	Of
	A
	Part Number

	Positions
	
	AMP
	YORK

	7
	0.7
	102241-5
	025-35971-000


[image: image75.png]



   CONTACTS     STANDARD PRESSURE
	Wire
	Wire
	Recom.
	Part Number

	Size
	Ins.
	Wire
	

	
	O.D.
	Strap
	AMP
	YORK

	
	
	Length
	
	

	24 - 20
	.069
	5/32
	1-87523-6
	025-35970-000


� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED Word.Picture.8  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���





� EMBED MSPhotoEd.3  ���











[image: image76.wmf]Number

Dim.

of

"A"

Positions

AMP

York

5

.778

640250-5

025-34503-000

6

.933

640250-6

025-25158-000

13

2.022

1-640250-3

025-34504-000

All dimensions are for reference purposes only.

Primary dimensions (  ) are American standard inches, 

BOLD PART NUMBER FOR GLOBALLY 

DESIGNED UNITS

* = Material (Thermoplastic, 94V-0)

Housing - Cap*

Part Number

metric millimeter dimensions are in brackets [  ]

[image: image77.png]


[image: image78.wmf]Wire

Recom.

Insulation

Wire

O.D.

Strip

AMP

York

Length

.043 - .110

5/32

640252-2

025-25157-000

Primary dimensions (  ) are American standard inches, 

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

metric millimeter dimensions are in brackets [  ]

All dimensions are for reference purposes only.

Part Number

Wire

Size



24 - 18

[image: image79.png]245

1622 |
100
[2.84)
7
A% 230
, [6.26) 15.84]
I Y
—d '\' L 050
725 [1.27)
{18.42)

097
(2.46]

'Mﬂ

156
(398"




[image: image80.wmf]Number

Dim.

of

"A"

Positions

AMP

York

5

.778

640426-5

025-33776-000

13

2.022

1-640426-3

025-33708-000

All dimensions are for reference purposes only.

Primary dimensions (  ) are American standard inches, 

BOLD PART NUMBER FOR GLOBALLY 

DESIGNED UNITS

* = Material (Thermoplastic, 94V-2)

Housing - Cap*

Part Number

metric millimeter dimensions are in brackets [  ]

[image: image81.png]i
(g

i
[



[image: image82.png]


[image: image83.wmf]Number

of

Dim.

Dim.

Positions

"A"

AMP

York

"B"

AMP**

York

2

.720

173063-2

025-28948-000

.811

173090-2

025-28951-000

3

.909

173065-2

025-28953-000

1.000

173091-2

025-28954-000

Primary dimensions (  ) are American standard inches, metric millimeter 

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

dimensions are in brackets [  ]

* = Material (PBT Black)

All dimensions are for reference purposes only.

Housing - Cap*

Housing - Plug*

** = Includes preassembled seal ring

Part Number

Part Number

[image: image84.png]


[image: image85.png]


[image: image86.wmf]Wire

Recom.

Insulation

Wire

O.D.

Strip

AMP

York

Length

.080 - .150

3/16

61347-2

025-19690-000*

Primary dimensions (  ) are American standard inches, 

metric millimeter dimensions are in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

All dimensions are for reference purposes only.

Part Number

Wire

Size



20 - 16

* = Fits .187 +/_.005 wide x .020 +/-.002 thick tab

[image: image87.wmf]AWG

Dia. (Inches)

CMA

AWG

Dia. (Inches)

CMA

4/0

0.460

212000.0

19

0.036

1290.0

3/0

0.410

168000.0

20

0.032

1020.0

2/0

0.365

133000.0

21

0.0285

810.0

1/0

0.325

106000.0

22

0.0253

642.0

1

0.289

83700.0

23

0.0226

509.0

2

0.258

66400.0

24

0.0201

404.0

3

0.229

52600.0

25

0.0179

320.0

4

0.204

41700.0

26

0.0159

254.0

5

0.182

33100.0

27

0.0142

202.0

6

0.162

26300.0

28

0.0126

160.0

7

0.144

20800.0

29

0.0113

127.0

8

0.128

16500.0

30

0.0100

101.0

9

0.114

13100.0

31

0.0089

79.7

10

0.102

10400.0

32

0.0080

63.2

11

0.091

8230.0

33

0.0071

50.1

12

0.081

6530.0

34

0.0063

39.8

13

0.072

5180.0

35

0.0056

31.5

14

0.064

4110.0

36

0.0050

25.0

15

0.057

3260.0

37

0.0045

19.8

16

0.051

2580.0

38

0.0040

15.7

17

0.045

2050.0

39

0.0035

12.5

18

0.040

1620.0

40

0.0031

9.9

Use to Convert Wire Gage to inches of Diameter, and CMA

To read mils direct, move decimal point three places to the right

All dimensions are for reference purposes only.

[image: image88.wmf]Terminal

CMA

Terminal

CMA

Connector

Range

Connector

Range

Size

Size

26 - 22

202 - 810

6

20800 - 33100

24 - 18 H.D.

320 - 2050

4

33100 - 52600

22 - 16

509 - 3260

2

52600 - 83700

22 - 14

509 - 5180

1/0

83700 - 119500

20 - 16 H.D.

810 - 3260

2/0

119500 - 150500

16 - 14

2050 - 5180

3/0

150500 - 190000

16 - 14 H.D.

2050 - 5180

4/0

190000 - 231000

16 - 10

2050 - 13100

250 - 300 MCM

231000 - 300000

14 - 12

3260 - 8230

300 - 350 MCM

300000 - 380000

12 - 10

5180 - 13100

400 MCM

380000 - 478000

8

13100 - 20800

500 - 600 MCM

478000 - 600000

AMP Range Chart

Use to select the proper size terminal or splice

[image: image89.wmf]Wire - Insulation Thickness

Straight

Flag

Two (2) #18 - 2/64

025-17076-000

N/A

Two (2) #16 - 2/64

025-17076-000

N/A

One (1) #16 - 2/64 & One (1) #16 - 4/64

N/A

N/A

One (1) #16 - 2/64 & One (1) #12 - 2/64

025-17076-000

N/A

Two (2) #14 - 2/64

025-17076-000

N/A

One (1) #14 - 2/64 & One (1) #12 - 2/64

N/A

N/A

Terminals

[image: image90.wmf]Wire Size Range

Insulation

Reference

AWG No.

Type

Symbol

Material

Table No.

22 to 10

Plasti-Grip

PG

Vinyl

3.5 (b)

22 to 10

Solistrand

SO

None

3.5 (c)

AMP Designation

[image: image91.wmf]Wire Size Range

AMP

Insulation

Reference

AWG No.

Designation

Material

Table No.

22 thru 2/0

Plastic-Grip

Vinyl

3.6 (b)

26 thru 10

Diamond Grip

Nylon

3.6 (c)

8 thru 2/0

Terminyl

Nylon

3.6 (d)

26 thru 2/0

Solistrand

None

3.6 (e)

[image: image92.png]€Min.

b c
Washer Washer
Radius Radius
Masx- Max.

Lo




[image: image93.png]


[image: image94.wmf]Wire

Wire

Type

Recom. Wire

Size

Insulation

AMP

York

Strip Length

O.D.

24 - 20

.055 - .094

Tab

173600-1

N/A

.157 - .177

Receptacle

171699-1

N/A

.157 - .177

Rubber Collar (Black)

172746-1

025-28950-000

N/A

20 - 16

.079 - .102

Tab

173706-1

025-28949-000

.157 - .177

Receptacle

173707-1

025-28952-000

.157 - .177

Rubber Collar (Grey)

172888-2

025-28957-000

N/A

All dimensions are for reference purposes only.

Primary dimensions (  ) are American standard inches, metric millimeter 

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

dimensions are in brackets [  ]

Part Number

* = Tab contact is for use in cap housing and receptable contact is for use 

    in plug housing

** = Rubber collar is crimped with insulation support of contact

[image: image95.wmf]Insulation

Color

AWG No.

Sym (*)

AWG No.

Sym (*)

AWG No.

Sym (*)

AWG No.

Sym (*)

AWG No.

Sym (*)

Red

22 - 16

*

8

8

2

2

3/0

3/0

Blue

16 - 14

*          *

6

6

0

0

4/0

4/0

Yellow

26 - 22

*

16 - 14HD

*

4

4

2/0

2/0

Yellow

12 - 10

*

Clear

24 - 20

*          *

Large

Heavy

* = The Sym. (Symbol) shown in this able indicates the marking left on the terminal to identify the tool used.

Insulated spring Spade and Ring-Tongue Terminals

Small

Medium

[image: image96.wmf]Wire

Stud

Recom.

Terminal

Size

Size

Nominal

Max.

Max

Min.

Wire

Wire

Supplied

AWG

No.

Width

Length

Clear

Insulation

Strip

No.

"W"

"L"

"E"

"C"

"X"

(O.D.)

Length 

±.008

Max.

AMP

York

22 - 16

6

0.234

0.811

0.666

0.250

0.140

0.140

.203 - .234

53240-2

025-19406-000

T

22 - 16

8

0.244

0.872

0.697

0.281

0.170

0.140

.203 - .234

53241-2

025-19407-000

T

22 - 16

8

0.375

0.921

0.746

0.281

0.170

0.200

.203 - .234

53950-3

025-19565-000

T

22 - 16

10

0.294

0.920

0.697

0.281

0.218

0.140

.203 - .234

53242-2

025-19408-000

T

22 - 16

10

0.294

0.969

0.746

0.281

0.218

0.200

.203 - .234

53242-6

025-19409-000

T

16 - 14

6

0.250

0.860

0.666

0.250

0.140

0.250

.203 - .234

52955-3

025-20519-000

T

16 - 14

6

0.250

0.811

0.666

0.250

0.140

0.170

.203 - .234

52955-1

025-18731-000

T

16 - 14

8

0.244

0.872

0.697

0.281

0.170

0.170

.203 - .234

53244-2

025-18732-000

T

16 - 14

8

0.244

0.921

0.746

0.281

0.170

0.250

.203 - .234

53244-4

025-19410-000

T

16 - 14

10

0.294

0.920

0.697

0.281

0.218

0.170

.203 - .234

53245-2

025-19376-000

T

16 - 14

10

0.406

0.969

0.746

0.281

0.218

0.250

.203 - .234

52957-3

N/A

T

16 - 14

1/4

0.437

1.102

0.759

0.345

0.338

0.150

.203 - .234

52423-2

025-19790-000**

T

12 - 10

8

0.312

1.052

0.877

0.276

0.170

0.250

.312 - .343

53247-2

025-19411-000

T

12 - 10

8

0.375

1.111

0.936

0.276

0.170

0.300

.312 - .343

52962-3

025-30995-000

T

12 - 10

10

0.406

1.100

0.877

0.276

0.218

0.200

.312 - .343

52963-1

N/A

T

12 - 10

10

0.375

1.278

0.965

0.305

0.308

0.300

.312 - .343

52475-3

N/A

T

12 - 10

1/4

0.437

1.289

0.946

0.345

0.338

0.250

.312 - .343

52433-1

025-19431-000

LP

** = Material (Nylon)

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

Primary dimensions (  ) are American standard inches, metric millimeter dimensions are in brackets [  ]

Terminal Supplied 

Part Number

Terminal Dimensions (in.)

All dimensions are for reference purposes only.

LP = Loose Piece

T = Tape Mounted

[image: image97.wmf]General

Adapter

Type

No.

Hole

"W"

"T"

"B"

"L"

"E"

Supplier

York

Tabs

Recept.

Dia.

2

1

Angle

6

-----

.250

-----

-----

-----

------

Kent     121209

025-10295-000

2

1

Straight

5

-----

.250

-----

-----

-----

------

AMP     61765-2

N/A

1

0

Straight

1

.177

.250

.295

-----

.715

.170

AMP     63038-2

N/A

1

0

Straight

1

.203

.250

.300

-----

.695

.141

Kent     121209

025-10437-000

1

0

Angle 90 degree

2

.171

.250

.295

.330

.440

------

AMP     42214-2

025-10185-000

1

0

Angle 90 degree

2

.171

.250

.409

.425

.462

.216

Kulka       KT81

025-18650-000

Marco     QC3236

1

0

Angle 45 degree

4

.171

.250

.295

.331

.375

------

AMP     60465-1

N/A

1

0

Angle 45 degree

4

.203

.250

.295

.331

.375

------

AMP     61365-1

025-10436-000

2

0

AU

3

.171

.250

.250

.390

.315

------

AMP     42802-1

025-15579-000

Primary dimensions (  ) are American standard inches, metric millimeter dimensions are in brackets [  ]

All dimensions are for reference purposes only.

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

Push-On Adapter Terminals have .250" x .032" Tabs, Tin Plated Brass

No. of Tabs or

Receptables

Dimensions

Part Numbers

[image: image98.wmf]Wire

Stud

Recom.

Terminal

Size

Size

Nominal

Max.

Max

Min.

Wire

Supplied

AWG

No.

Width

Length

Clear

Strip

No.

"W"

"L"

"E"

"C"

"X"

Length 

AMP

York

22 - 16

6

0.234

0.576

0.431

0.250

0.140

1/4

53830-2

025-19432-000

T

22 - 16

8

0.244

0.637

0.462

0.281

0.170

1/4

53831-2

025-19433-000

T

22 - 16

10

0.294

0.685

0.462

0.281

0.218

1/4

53832-2

025-19434-000

T

16 - 14

6

0.250

0.576

0.431

0.250

0.140

1/4

53123-2

025-19435-000

T

16 - 14

8

0.244

0.637

0.462

0.281

0.170

1/4

53833-2

025-18579-000

T

16 - 14

10

0.294

0.685

0.462

0.281

0.218

1/4

53834-2

025-19436-000

T

16

1/4

0.437

0.822

0.536

0.350

0.281

1/4

53875-2

025-34201-000

T

[1.5]

[M6]

[11.1]

[20.88]

[13.61]

[8.89]

[7.14]

[6.35]

12 - 10

6

0.250

0.636

0.452

0.174

0.179

5/16

53126-2

N/A

T

12 - 10

8

0.375

0.729

0.554

0.276

0.170

5/16

53127-2

N/A

T

12 - 10

10

0.312

0.777

0.554

0.276

0.218

5/16

53836-2

025-19438-000

T

12 - 10

1/4

0.375

0.902

0.616

0.338

0.281

5/16

53837-2

025-19439-000

T

12-10

1/4

0.375

0.902

0.616

0.358

0.281

1/4

53837-2

025-33797-000

T

[4-6]

[M6]

[9.53]

[22.91]

[15.65]

[8.59]

[7.14]

[6.35]

Primary dimensions (  ) are American standard inches, metric millimeter dimensions are in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

Terminal Supplied 

Terminal Dimensions (in.)

Part Number

All dimensions are for reference purposes only.

LP = Loose Piece

T = Tape Mounted

[image: image99.wmf]Number

Dim.

of

"A"

Circuits

AMP

York

AMP

York

2  (In-Line)

-----

1-480698-0

025-19672-000

1-480699-0

025-21159-000

3  (In-Line)

0.800

1-480700-0

025-19671-000

1-480701-0

025-21193-000

4  (In-Line)

1.050

1-480702-0

025-21417-000

1-480703-0

025-21756-000

5  (In-Line)

1.300

1-480763-0

N/A

1-480764-0

N/A

6

-----

1-480704-0

025-19670-000

1-480705-0

025-20963-000

6  (In-Line)

-----

640585-1

025-32566-000

926307-1

025-35141-000

8  (In-Line)

2.050

640586-1

025-28388-000

926308-1

N/A

9

0.800

1-480706-0

025-21192-000

1-480707-0

025-21191-000

10  (In-Line)

2.550

926302-1

N/A

926309-1

N/A

12

1.050

1-480708-0

025-21196-000

1-480709-0

025-20787-000

15

1.300

1-480710-0

025-20918-000

1-480711-0

025-20788-000

Primary dimensions (  ) are American standard inches, 

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

metric millimeter dimensions are in brackets [  ]

* = Material (Nylon 94V-2 Natural Color)

All dimensions are for reference purposes only.

Housing - Plug*

Housing - Cap*

Part Number

Part Number

[image: image100.wmf]Wire

**

Recom.

Terminal

Size

Stud

+/- .008

Max.

Min.

Max.

Wire

Wire

Supplied

AWG

Size

Hole

Width

Length

Clear

Washer

Insulation

Strip

No.

No.

"H"

"W"

"L"

"C"

Radius

(O.D.)

Length 

Max.

AMP

York

22 - 16

6

0.145

0.218

0.672

0.156

0.140

.203 - .234

36150

025-06956-000

LP

22 - 16

6

0.145

0.312

0.797

0.250

0.140

.203 - .234

36152

025-28964-000

LP

22 - 16

8

0.171

0.312

0.844

0.281

0.140

.203 - .234

31890

025-09018-000

LP

22 - 16

10

0.197

0.281

0.844

0.281

0.140

.203 - .234

36154

025-09043-000

LP

22 - 16

 1/4

0.265

0.469

1.078

0.437

0.125

.203 - .234

320571

025-28689-000

LP

16 - 14

6

0.145

0.343

0.859

0.281

0.150

.203 - .234

36157

025-14663-000

LP

16 - 14

6

0.145

0.250

0.703

0.171

0.150

.203 - .234

320561

025-28965-000

LP

16 - 14

6

0.145

0.281

0.953

0.219

.250 (*)

.203 - .234

35634

025-18153-000

LP

16 - 14

8

0.171

0.343

0.859

0.281

0.170

.203 - .234

320565

025-13230-000

LP

16 - 14

10

0.197

0.343

0.859

0.281

0.150

.203 - .234

320574

025-04811-000

LP

16 - 14

10

0.197

0.343

0.859

0.281

0.170

.203 - .234

36160

025-05628-000

LP

16 - 14

10

0.197

0.343

1.046

0.281

.250 (*)

.203 - .234

34805

025-09650-000

LP

16 - 14

1/4

0.265

0.531

1.296

0.437

.250 (*)

.203 - .234

34806

025-08788-000

LP

**

"H" Hole Tolerance

LP = Loose Piece

Stud Size  

³ 1/4 = 

±

 

.005

Stud Size  

£

 1/4  = 

±

 .003

Terminal Supplied 

Primary dimensions (  ) are American standard inches, metric millimeter dimensions are in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

Part Number

Terminal Dimensions (in.)

All dimensions are for reference purposes only.

T = Tape Mounted

* = Indicates heavy duty terminals

[image: image101.wmf]Type

Wire

Recom.

Size

Width

Width

Length

Wire

Wire

AWG

Inside

Outside

Overall

Insulation

Strip

No.

"T"

"W"

"L"

(O.D.) *

Length 

"D"

AMP

York

Straight

22 - 18

0.090

0.300

0.750

.090 - .130

1/4

41772

025-06874-000

Straight

18 - 14

0.065

0.300

0.755

   .120 - .170***

1/4

41274

025-06642-000

Straight

18 - 14

0.124

0.318

0.750

   .120 - .170

1/4

41832

025-14291-000

Straight

16 - 12

0.065

0.300

0.822

.210 - .265

1/4

41728

025-30998-000

Straight

14 - 10

0.065

0.300

0.775

.225 - .275

1/4

60635-1

025-17076-000

Flag

18 - 12

0.124

0.318

.670 Max.

.110 - .210

7/32

41802

025-06759-000

Flag

12 - 10

0.124

0.318

.670 Max.

.110 - .210

7/32

42563-8

025-13812-000

Straight**

18 - 14

0.115

0.300

0.770

.120 - .170

7/32

61944-2

025-11190-000

Straight**

14 - 10

0.105

0.300

0.770

.150 - .200

7/32

62253-2

025-19990-000

Primary dimensions (  ) are American standard inches, metric millimeter dimensions are 

in brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

*     = Wire insulation O.D. is given for those terminals having insulation support

**   = Terminal called a "Piggy-Back", having a male-tab on back side to receive an 

*** = When wire insulation diameter exceeds  listed range for terminal, use terminal 

      025-14291-000; Also see Application, Paragraph 7.4(e)

FITS .250" x .032" MALE TAB

Part Number

Terminal Dimensions (in.)

All dimensions are for reference purposes only.

       extra female terminal

[image: image102.wmf]Type

Wire

Recom.

Remarks

Size

Width

Width

Length

Wire

Wire

AWG

Inside

Outside

Overall

Insulation

Strip

No.

"T"

"W"

"L"

(O.D.) *

Length 

"D"

AMP

York

Straight

18 - 16

0.065

0.301

.805 Max.

.120 - .170

1/4

41729

025-08188-000

Loose Piece

Straight

18 - 14

0.115

0.300

0.780

.150 - .210

1/4

42692-2

025-25920-000

Straight

14 - 10

0.124

0.318

0.770

.150 - .200

1/4

42437-2

025-09455-000

Primary dimensions (  ) are American standard inches, metric millimeter dimensions 

are in brackets [  ]

All dimensions are for reference purposes only.

BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS

FITS .250" x .032" MALE TAB

Terminal Dimensions (in.)

Part Number

[image: image103.png]


[image: image104.png]


[image: image105.png]


[image: image106.wmf]Wire

Stud

Recom

.

Size

Size

Max.

Max.

Wire

Wire

AWG

No.

Hole

Width

Length

Washer

Insulation

Strip

No.

"H"

"W"

"L"

Radius

(

O.D.)

Length

± 

.005

± 

.008

"C"

Max.

AMP

York

2

5/16

0.328

0.711

2.063

0.578

.473 max.

.453 - .484

324112

025-28684-000

1/0

1/4

0.265

0.807

2.426

0.625

.580 max.

.735 - .859

324056

025-28683-000

Primary dimensions 

(  ) are American standard inches, metric millimeter dimensions are in

brackets [  ]

BOLD PART NUMBER FOR GLOBALLY DESIGNED

UNITS

Part Number*

* = Indicates heavy duty

terminals

All dimensions are for reference purposes

only.

Terminal Dimensions

(in.)

_994573944.bin

_994577490.bin

_994672464.bin

_1076909638.doc


Wire







Stud







Recom.







Size







Size







Max.







Max.







Wire







Wire







AWG







No.







Hole







Width







Length







Washer







Insulation







Strip







No.







"H"







"W"







"L"







Radius







(O.D.)







Length 















.005















.008







"C"







Max.







AMP







York







2







5/16







0.328







0.711







2.063







0.578







.473 max.







.453 - .484







324112







025-28684-000







1/0







1/4







0.265







0.807







2.426







0.625







.580 max.







.735 - .859







324056







025-28683-000







Primary dimensions (  ) are American standard inches, metric millimeter dimensions are in brackets [  ]







BOLD PART NUMBER FOR GLOBALLY DESIGNED UNITS







Part Number*







* = Indicates heavy duty terminals







All dimensions are for reference purposes only.







Terminal Dimensions (in.)












_1098789216.bin

_1077081384.bin

_1050236355.bin

_1076908703.bin

_1047789340.bin

_994581592.bin

_994660889.bin

_994662259.bin

_994662749.bin

_994663488.bin

_994662472.bin

_994661946.bin

_994660456.bin

_994579830.bin

_994581448.bin

_994578071.bin

_994576472.bin

_994576812.bin

_994577388.bin

_994576638.bin

_994574861.bin

_994576342.bin

_994574712.bin

_994569399.bin

_994571197.bin

_994573677.bin

_994573857.bin

_994572688.bin

_994573558.bin

_994570917.bin

_994505862.bin

_994568942.bin

_994569165.bin

_994503464.bin

