PRIVATE 


19XL/XT, 19EX, 19XR/XRT 
C9619

     HIGH VOLTAGE TERMINAL INSTALLATION



   7/05/96












       New

PURPOSE:


Procedure for assembling and installing the new ceramic high


voltage terminals (See figure 1). Part number 02XB05003001.

BACKGROUND:


Production has now made the change to the new ceramic terminal


on 19 series high voltage motors. These replace the plastic 


terminals who’s installation was outlined in C9504. The 


following procedure is for the assembly and installation of 


the new ceramic high voltage terminal only.

GENERAL INFORMATION:


The new ceramic terminal can be used as a direct replacement 


for the plastic terminal without changing the stud.


Replacement terminal studs are available if necessary through 


RCD. The part number is 19XR660018 (see figure 2). The hole in 


the end of the stud is .25 in. (6.4 mm) diameter by .5 in. 


12.7 mm) deep. It maybe necessary to enlarge it to accommodate 


larger wires. This stud also requires a 2 bolt connector lug 


part number 02XB05002901) for making electrical connections to 


the terminal.

INSTALLATION:

1. Inspect and clean the terminal and  the machined mating surface of the motor shell or terminal plate with emery cloth or fine sand paper to ensure a leak tight assembly. Lubricate insulator o-ring and mating surface with o-ring lubricant (Parker Super O lube).

2. Slide insulator over the motor lead and thread insulator into motor housing. Torque insulator to 50 ft-lbs (68 Newton-Meters).

3. Lubricate terminal stud o-ring and slide the o-ring over the threaded portion of copper stud, then install the copper sleeve.

FILE:

COMPRESSOR-MOTOR-DRIVE-GEARS

C9619

PAGE 2

IMPORTANT: The copper sleeve which contacts the o-ring, packaged with the terminal, has been selected to properly fit the ceramic terminal body inside diameter. Do not mix terminal insulators and sleeves, use only the sleeve provided with each individual terminal.
4.
Slide the copper washer over the stud and next to the copper


sleeve. (If replacing an old plastic terminal and not the 


terminal stud two washers will be necessary because of the 


difference in length between the two insulators.)

5.
Install the brass jam nut and tighten against the washer(s) to


a maximum of 3 ft-lbs (4 Newton-Meters) while holding copper 


stud. This will seat copper washer against insulator and draw 


internal shoulder on copper stud against the internal edge of 


insulator.

6.
If leakage occurs after the terminal is assembled, then the 


parts are defective and should be replaced. Do not over 


tighten in an attempt to eliminate leaks.

