














	23XL Lifting Warning Label	C9622


	11/20/96


	None


		23XL














PURPOSE:





To inform the field of the proper method of lifting disassembled components of screw compressors in the field and of a program to provide lifting warning labels for all 23XL compressors.





23XL COMPRESSOR COMPONENT INSTRUCTIONS:





Metric threaded eye bolt holes are provided on each component of the compressor assemblies as an aid in lifting the individual compressor castings only.  Use cables or slings to rig the entire compressor.  Do not use English eye bolts or bodily injury or property damage can occur.  Refer to the following chart for eye bolt sizes for frame 1, 2, and 4 compressors:








Compressor�
Compressor Capacity


Refrigeration Tons�
Eye Bolt Size�
�
TC�
160, 200, 250�
M16 x 2.0  27mm, 35mm  680kg


(1500 lbs)�
�
TD�
300, 350�
M20 x 2.5  30mm, 45mm  900kg


(2000 lbs)�
�






Lifting warning labels (part # 23XL05006201) for all 23XL chillers have been shipped to the Carrier service managers. The label (depicted in figure 1) is to be wire tied on the oil supply line at the top of the discharge casing or can be molded to the shape of the casting and adhered by double sided tape around the lifting hole (as depicted by fig. 2).








EXTRA LABELS ARE AVAILABLE FROM CAES SERVICE ENGINEERING.








FILE: COMPRESSOR - MOTOR - DRIVE - GEARS





�











 





 











