









	19XL MOTOR END BELL O-RING    	C9637�PRIVATE ��

	10/23/96



			19XL



PURPOSE:



To clear up confusion concerning the motor end bell O-ring during a motor stator replacement on the 19XL line of centrifugal chillers.



BACKGROUND:



The original 19XL centrifugal chillers were released with a cast iron motor end bell. This cast end bell had a machined O-ring groove around the inboard side to provide for a seal against the motor stator housing. The part number of cast end bell is 02XB35001001 and the O-ring used to provide the seal is KK71EW470. In September of 1995 a change was made to the design of the end bell. The end bell changed from an intricate cast iron design to a more straightforward section of steel. The part number of the steel end bell is 02XB35032501. To eliminate extra processing steps on the steel end bell the O-ring groove was moved from the end bell to the motor stator housing. A new O-ring was selected, part number KK71EW471.  



INFORMATION:



With the changes described above the possibility exists of replacing a motor stator on an old 19XL (without an O-ring groove)  with a new stator that has an O-ring groove machined in it. The new stator and the old cast end bell have been designed such that the grooves do not align with each other hence the different O-ring part numbers. If this situation does occur it is perfectly acceptable to use either the KK71EW470 or the KK71EW471. If the existing O-ring is suitable for reuse it is acceptable in the application. If a replacement is needed I suggest using the KK71EW471 because it is mounted to the stator and you don’t have to worry about the O-ring moving while rigging the cover back into place. When replacing a stator on a chiller built after September of 1995 the only choice is using the KK71EW471, so it also covers more applications. Refer to the table below for application. 



O-RING APPLICATION TABLE



APPLICATION�KK71EX470�KK71EW471��OLD STATOR & OLD END BELL�ACCEPTABLE�UNACCEPTABLE��NEW STATOR & OLD END BELL�ACCEPTABLE�ACCEPTABLE��NEW STATOR & NEW END BELL�UNACCEPTABLE�ACCEPTABLE��



FILE: SPECIFIED PARTS



�







 



 










