














MOTOR TERMINAL LUGS 	C9702


	1/23/97


												C8701


		ALL HERMETIC CHILLERS					   3/10/87








PURPOSE:





To give updated part numbers for motor terminal lugs by AMP Inc., Thomas and Betts, and Burndy, along with phone numbers for product information.





BACKGROUND:





The following tables list standard AMP, Thomas and Betts, and Burndy terminal lugs for wire sizes from 6 AWG through 600 MCM.  The lugs are crimped on the power wires using a crimping tool, and have one or two holes. The 1-hole lugs will mount directly to the motor terminal studs, and will accomodate the stud sizes indicated in the list.  The 2-hole lugs all have 1/2" holes, and are mounted to the current high voltage lug adapter (PN 02XB05002901) using two 1/2" bolts.  This high voltage lug adapter is threaded to the 9/16" stud on the motor, and is used on all current high voltage chillers.





INFORMATION:





AMP Inc. (Phone 800-522-6752)





Wire Size		5/8" Stud	3/4" Stud	7/8" Stud	1/2" Studs


			1-hole	1-hole	1-hole	2-holes  


                                                              


6AWG			36809		36810                              


4AWG			35669		35670                              


3AWG                                                         


2AWG			320754	320755                             


1AWG                                                         


1/0AWG		320744	320748			53680-2  


2/0AWG		322224	322225			53681-2  


3/0AWG		322222	322223			53682-2  














FILE:		Controls - Wiring


�
C9702


Page 2





Wire Size		5/8" Stud	3/4" Stud	7/8" Stud	1/2" Studs


			1-hole	1-hole	1-hole	2-holes  


                                                              


4/0AWG		322227	322228	321625	53683-2  


250MCM		323050	323140			327258   


300MCM		323050	323140			53684-2  


350MCM		324105	322428			53641-2  


400MCM		324202	323222


500MCM		322270	322271			53642-2             


600MCM		322270	322271     


                                                                   


Thomas and Betts (Phone 901-682-7766)


                                                                  


Wire Size		5/8" Stud	1/2" Studs		1/2" Studs (Long Barrel Type)


			1-hole	2-holes		2-holes                        


                                                                       


2/0AWG				54476			54862BE                        


3/0AWG				54478			54864BE                        


4/0AWG		58166		54479			54866BE                        


250MCM				54480			54868BE                        


300MCM		54181					54870BE                        


350MCM		54183		54482			54872BE                        


400MCM		54185					54874BE


500MCM		54187		54484			54876BE                


600MCM		54120					54878BE                


                                                                  


Burndy (Phone 800-346-4175)


                                                                  


Wire Size		5/8" Stud	3/4" Stud	7/8" Stud	1/2" Studs   


			1-hole	1-hole	1-hole	2-holes      


                                                                  


6AWG									YA6C-2N      


4AWG									YA4C-2N      


3AWG									YA3C-2N      


2AWG									YA2C-2N      


1AWG									YA1C-2N      


1/0AWG								YA25-2N      


2/0AWG		YA26-L7	YA26-L60			YA26-2N


3/0AWG								YA27-2N                 


4/0AWG		YA28-L17	YA28-L56			YA28-2N                 


250MCM						YA29L-TC78	YA29-2N                  


300MCM		YA30-L7			YA30-L27	YA30-2N                 


350MCM		YA31-L7			YA31-L36	YA31-2N                 


400MCM		YA32-L			YA32L-TC78	YA32-2N                 


500MCM		YA34-L	YA34-L8	YA34-L9	YA34-2N                 


600MCM		YA36-L			YA36L-TC78	YA36-2N              


                                                                       








NOTE: Part numbers are taken from current manufacturer's catalogs and are subject to change.  Selection of parts must be confirmed with the manufacturer before an order is placed.





Terminal lugs which are not available may be made by drilling available lugs to required size, as long as adequate stock remains.


�











 





 











