1
C9702A
Motor Terminal Lugs
3 of 3


[image: image1.wmf]
SERVICE BULLETIN




Carrier Corporation




[image: image2.png]Typical 1 - Hole Lug




	Number:   C9702A
	Date:  06/25/2003
	Supersedes: C9702

	
	
	

	Title:  Motor Terminal Lugs

	
	
	

	Author: Steve Bayes 
	
	Dept: North American Commercial 

	
	
	     Service Engineering

	Category: General
	
	

	
	
	

	Dealer Bulletin Number:  none                 
	
	


MODELS AFFECTED:
Carrier:  All Hermetic Chillers 

PURPOSE: 

To give updated part numbers for motor terminal lugs by Tyco Electronics (AMP brand), Thomas and Betts, and FCI (Burndy), along with phone numbers for product information.

BACKGROUND:

The following tables list standard Tyco (AMP), Thomas and Betts, and FCI (Burndy) terminal lugs for wire sizes from 6 AWG through 600 MCM.  The lugs are crimped on the power wires using a crimping tool, and have one or two holes. The 1-hole lugs will mount directly to the motor terminal studs, and will accommodate the stud sizes indicated in the list.  The 2-hole lugs all have 1/2" holes, and are mounted to the current high voltage lug adapter (P/N 02XB05002901) using two 1/2" bolts.  This high voltage lug adapter is threaded to the 9/16" stud on the motor, and is used on all current high voltage chillers.

INFORMATION:

Tyco Electronics (AMP brand)   (Phone 800-522-6752)

	Wire Size:
	5/8" Stud
	3/4" Stud
	7/8" Stud
	1/2" Studs

	
	1-hole
	1-hole
	1-hole
	2-holes

	6AWG
	36809
	36810
	
	

	4AWG
	35669
	35670
	
	

	3AWG
	
	
	
	

	2AWG
	320754
	320755
	
	

	1AWG
	
	
	
	

	1/0AWG
	320744
	320748
	
	53680-2

	2/0AWG
	322224
	322225
	
	53681-2

	3/0AWG
	322222
	322223
	
	53682-2


Tyco (AMP) continued)

	Wire Size:
	5/8" Stud
	3/4" Stud
	7/8" Stud
	1/2" Studs

	
	1-hole
	1-hole
	1-hole
	2-holes

	4/0AWG
	322227
	322228
	321625
	53683-2  

	250MCM
	323050
	323140
	
	327285

	300MCM
	323050
	323140
	
	53684-2

	350MCM
	324105
	322428
	
	53641-2

	400MCM
	324202
	323222
	
	

	500MCM
	322270
	322271
	
	53642-2

	600MCM
	322270
	322271
	
	


Thomas and Betts   (phone 800-816-7809)

FAX orders to 800-816-7810

	Wire Size:
	5/8" Stud
	1/2" Studs
	1/2" Studs (Long Barrel Type)

	
	1-hole
	2-holes
	2-holes

	2/0AWG
	
	54476
	54862BE

	3/0AWG
	
	54478
	54864BE

	4/0AWG
	58166
	54479
	54866BE

	250MCM
	
	54480
	54868BE

	300MCM
	54181
	
	54870BE

	350MCM
	54183
	54482
	54872BE

	400MCM
	54185
	
	54874BE

	500MCM
	54187
	54484
	54876BE

	600MCM
	54120
	
	54878BE


FCI (Burndy)   (Phone 800-346-4175)

	Wire Size:
	5/8" Stud
	3/4" Stud
	7/8" Stud
	1/2" Studs

	
	1-hole
	1-hole
	1-hole *
	2-holes

	6AWG
	
	
	
	YA6C-2N

	4AWG
	
	
	
	YA4C-2N

	3AWG
	
	
	
	YA3C-2N

	2AWG
	
	
	
	YA2C-2N

	1AWG
	
	
	
	YA1C-2N

	1/0AWG
	
	
	
	YA25-2N

	2/0AWG
	YA26-L7
	YA26-L60
	
	YA26-2N

	3/0AWG
	
	
	
	YA27-2N

	4/0AWG
	YA28-L17
	YA28-L56
	
	YA28-2N

	250MCM
	
	
	YA29L-TC78
	YA29-2N

	300MCM
	YA30-L7
	
	YA30-L27
	YA30-2N

	350MCM
	YA31-L7
	
	YA31-L36
	YA31-2N

	400MCM
	YA32-L
	
	YA32L-TC78
	YA32-2N

	500MCM
	YA34-L
	YA34-L8
	YA34-L9
	YA34-2N

	600MCM
	YA36-L
	
	YA36L-TC78
	YA36-2N


Notes: 

· Part numbers were rechecked as valid on 4/29/2003 and are subject to change.  Selection of parts must be confirmed with the manufacturer before an order is placed.  

· FCI / Burndy parts marked * are considered “special make”.

· Terminal lugs which are not available may be made by drilling available lugs to required size, as long as adequate stock remains.

[image: image3.png]Typical 2 - Hole Lug

[ s 1 F




[image: image4.png]#.531

1.00—p+—=

FULL THREAD

(.57)—+

9/16-18 UNF-.

TAP DRILL 1.4

28
DEEP

L750—






POLICY: 

N/A

� EMBED MSPhotoEd.3  ���








� EMBED MSPhotoEd.3  ���








Current High Voltage Lug





� EMBED PBrush  ���








FILE: CONTROLS & WIRING


_1118040947.bin

_1118041027.bin

_1118041137

_1074335172.doc


�












