









	    O-RING - HOLLOW HEX PLUG	C9703�PRIVATE ��

     	3/26/97

	  NEW

               23XL Frame 1, 2 and 4





Purpose:



Inform the field about an O-ring material change on the hollow hex plugs used on 23XL compressors.                                      

                                                                                

Machines Affected:



All 23XL chillers shipped prior to November 1996.           



Background:



Some hex plug o-rings have been tan or black colored Viton material.  For consistancy and long term reliability with any mix of refrigerant and oil all replacement o-rings are neoprene.



Field Action:



If hex plug o-ring leaks are found or the refrigerant has been transfered to the condenser or storage tank in order to perform maintenance or repairs it is recommended then to remove all the hollow hex plugs from the compressor and replace all the O-rings with new ones and reinstall the plugs.  Three of the plugs are hidden under insulation see sketch for location of the plugs.

                                                            

Parts:	Qt		Part Number	use on size		location              

                                                                                

		5		KK71EW-904		7/16 - 20 plug		see sketch             

		2		KK71EW-906		9/16 - 18 plug		see sketch             

		1		KK71EW-912		1 1/16 - 12 plug	Economizer port Fr 1&2

		1		KK71EW-914		1 3/16 - 14 plug	Economizer port Fr 4 



   Note: Total quantity will vary between 6 and 8 depending on model of the chiller and compressor size.  Listing above will cover any combination.        

                                                   

SAMS II fault code: 9703







FILE:		Specified Parts

�







 



 










