














	   BUTTERFLY ISOLATION VALVES	C9708�PRIVATE ��


     	4/7/97


	  NEW


               ALL CHILLERS WITH BUTTERFLY ISOLATION


               VALVES





                                                                              


PURPOSE:     


                                                                              


To provide information for re-assembly of butterfly type    isolation valves after a machine has been separated for installation, or following service which requires removal of a valve.                  


                                                                              


INFORMATION:                                                                  


The butterfly type valves have a ring (seat) that makes contact with the disc.  If the ring is not flush with the surface of the valve, it could become "wedged" at an angle, preventing the valve from making a proper seal with the flange, and possibly causing damage to the valve.  For these reasons, it is important to remove and re-install the valve in the CLOSED position only, making certain that both sides are flat, with no components (such as the ring) protruding. Also, note the proper flow direction for the valve before removing it, and make sure it is re-installed in the same orientation.  The flange bolts should be torqued in a staggered (cross) pattern.  NOTE: When a chiller (such as the 19XL) is designed to ship with refrigerant in the condenser, the isolation valve is installed with the flow arrow pointing back toward the compressor discharge because the valve provides a stronger seal in that direction.  The flow arrow direction does not matter during operation.





The valves are manufactured by Xomox or Neles-Jamesbury and the general information above applies to both types of valves.  If more specific information is necessary, the valve
