














	23XL - FRAME 4 SLIDE ROD CHANGE	C9709�PRIVATE ��


     	4/15/97


	  NEW


               23XL





Purpose:





This bulletin is to advise the field that after October, 1996, a new capacity slide rod with adjustable locknuts was introduced on 23XL frame 4, fixed V.I. compressor.


                                                                                


Compressor Affected:





D40 and D60 only.


Compressor starting s/n 5096V-----.                      


                                                                                      


Reference: Bulletin C9602A                                           


                                                                                


Recommendation:





To improve long term reliability, the latest design adjustable locknuts should be installed on compressor built prior to November 1996 which experience premature locknut failures.





Procedure:





Apply 3 drops of green Loctite (Retaining Compound) to the male threads, on both ends of the capacity shaft, at 120 degree increments.


Remove the 4 set screws from both locknuts.  Install both locknuts and torque  the main body to 75 ft-lbs (102 Nm).  Two locknut sockets p/n TS-144504D (see sketch) will be required.


Apply 1 drop of green Loctite on each set screw and reinstall set screws into the main nut body.


Torque the four set screws, in an even pattern, to 32 in-lb (4 Nm).





Note:  Make sure all parts are clean and degreased as per Loctite's instructions.





Parts:





Compressor size -                     D60             D40


Slide rod  p/n                        1TD0216D        1TD0213D


Adjustable locknut p/n (2 required)   KT51HZ100       KT51HZ100





Loctite 603  - Loctite p/n 21440 for 10ml bottle


               Other acceptable Loctite 675 & Loctite 609


FILE: Compressor


�











 





 














