









	     SHRINK WRAP FOR MOTOR TERMINALS	C9714�PRIVATE ��

     	4/30/97

	  NEW

                  ALL WITH UNIT-MOUNTED STARTERS





PURPOSE:



To provide information for the proper removal and installation  of shrink wrap (insulating sleeve) on motor terminals.               



BACKGROUND:



All chillers with factory installed unit-mounted starters are presently shipped with shrink wrap on the motor terminals.  The shrink wrap is P/N LF33MM112 and is 1 piece, 12 inches in length.  For replacement, it is necessary to order 3 pieces and cut them in half for a total of 6 pieces, 6 inches in length.                    

                                                                              

 INFORMATION:                                                       

                                                                              

To soften shrink wrap for removal, a heat gun (or electric hair dryer) should be used.  Because the ceramic insulator on the motor terminals cannot exceed 220 Degrees F (at higher temperatures the ceramic will crack and leak) the heat gun must be kept moving at all times to avoid excessive localized heat.



CAUTION: At no time should a torch, lighter, or similar localized heat source be used on the shrink wrap.             













                                               

 FILE: CONTROLS - WIRING                                                                                                                              �

�







 



 










