









	23XL SLIDE VALVE SPRING RETAINER (SHAFT)	C9715�PRIVATE ��

     	5/12/97

	  NEW

               ALL 23XL (FRAME 1, 2 & 4)





PURPOSE:                                                            






To inform that the slide valve spring retainer (shaft)
 
i
s now being made of a harder material than was used previously.  



                                                                       


BACKGROUND:






When a machine runs loaded, the unloader spring is tightly compressed 
 on the retainer (shaft).  When the machine is unloaded, the spring is 
 not compressed as tightly, and suction gas flowing over it may cause 
 it to vibrate and wear the retainer.  This wear is normal, and could 
  create "notches" or "ripples" where the coils of the spring contact 
the retainer, or could appear to "shave" material from the retainer. 






INFORMATION:                
                                          



                                                                             


The wear exhibited by the spring retainer (shaft) is not considered 
detrimental to reliable compressor operation.  It has not caused any 
compressor failures.






RCD stocks only the new, harder retainer.  The part number will 
remain the same (1TC0228C) and applies to all machines (frames 1,2 & 4).

















FILE:
 COMPRESSOR-MOTOR-DRIVE-GEARS



�







 



 













