














	19XR HIGH SPEED SHAFT CHANGE	C9718�PRIVATE ��


	10/30/97


												  NEW


			19XR FRAME 3 AND 4





PURPOSE:





To inform the field of a change in the diameter of the high speed shafts on frame 3 and frame 4 19XR compressors.





GENERAL INFORMATION:


The initial release of the smaller capacity frame three and frame four 19XR compressors were released with a high speed shaft that measured 1.15” at the impeller mounting end of the shaft. As further testing was completed on larger tonnage frame three and four compressors it was found that the impeller could deflect during operation. To increase the overall strength of the shaft the diameter was changed to 1.37”. Approximately 8/97 all production units utilized the new large diameter shaft.





SERVICE PARTS


Service parts only stocks the new larger diameter shaft and associated impellers for frame three and frame four compressors. When ordering replacement parts it will be necessary to check the diameter of the shaft (see figure 1) before ordering the parts needed for the repair (i.e. if the machine has a small diameter shaft and either the shaft or impeller needs to be replaced, a new shaft, impeller spacer, and shim pack, etc. will need to be ordered).




















Figure 1. High Speed Shaft


The table below outlines the large diameter high speed assembly part numbers along with the other associated parts that will need to be ordered if replacing a small diameter with a large diameter. The large diameter shaft will work with a small diameter thrust housing assembly.





PART NAME�
FRAME 3 COMPRESSOR�
FRAME 4 COMPRESSOR �
�
HI SPD BRG & SHAFT ASSY 60 HZ�
02XR34000201�
02XR44000701�
�
HI SPD BRG & SHAFT ASSY 50 HZ�
02XR34000202�
02XR34000702�
�
HIGH SPEED SHAFT 60 HZ�
02XR35008401�
02XR45008601�
�
HIGH SPEED SHAFT 50 HZ�
02XR35008402�
02XR45008602�
�
SPACER�
02XR35006801�
02XR35006801�
�
KEYS�
(2) 02XR35005701�
(2) 02XR45006502�
�
ROLL PIN�
(2) AX14CA064�
(2) AX14CA096�
�
IMPELLER NOSE PIECE�
02XR35008701�
02XR45009201�
�
IMPELLER CAP SCREW�
AA44AA269�
AA44AA267�
�
IMPELLER WASHER�
02XB05002701�
02XB05002702�
�
SHIM�
02XR35008601�
02XR35006901�
�
IMPELLER�
CONTACT RCD�
CONTACT RCD�
�
Table 1 Large Diameter Parts List


�











 





 











