









	   17/19EX REVISED R-134A REFRIGERANT CHARGE	C9723�PRIVATE ��

     	7/22/97

	  NEW

               17/19EX





Purpose:



This bulletin is intended to provide information regarding the revised 

R-134a refrigerant charges for the 17/19EX machines.  This bulletin was originally released to the field sales organization as bulletin 

17/19EX-97-06.  The current product literature will be corrected at reprint.



Information:



The following tables represent the current and old R-134a refrigerant charge values for all 17/19EX heat exchangers.  The total machine charge can be calculated from the tables and will appear on the unit nameplate. These values are estimates for total charge amounts.   Final refrigerant charge amounts will depend on job conditions, and may require trimming by the start-up technician.   Below is an  example of how to calculate the amount of refrigerant charge for a 17EX4857 unit.



Vessel�Charge (lb)��Charge (kg)��48 Cooler (from Table 1)�2540��1152��57 Condenser (from � REF _Ref394125084 \* MERGEFORMAT �Table 2�)�1420�� 644��Economizer (from � REF _Ref394125122 \* MERGEFORMAT �Table 3�)� 840�� 381��Total�4800��2177��



Recently shipped machines may not have nameplate charge amounts that match the expected values from the E-Cat, Product Data, Installation Instructions, or Start-Up, Operation and Maintenance Instructions values. If there is any doubt as to the amount of charge required on a recently shipped unit, check the unit nameplate or contact your order correspondent.









File:  Installation, Start-Up, & Operation

�Table � SEQ Table \* ARABIC �1� - Cooler Refrigerant Charge

Cooler�������Refrigerant (R-134a)������Current��Old���Code�lbs�kg�lbs�kg��31�1690�766�1540�698��32�1790�812�1640�744��33�1890�857�1740�789��41�1990�902�1900�862��42�2090�948�2000�907��43�2190�993�2100�952��44�1400�635�2190�993��45�2060�934�2260�1025��46�2160�980�2360�1070��47�2260�1025�2460�1116��48�2540�1152�2540�1152��









































Table � SEQ Table \* ARABIC �2� - Condenser Refrigerant Charge

Condenser�������Refrigerant (R-134a)������Current��Old���Code�lbs�kg�lbs�kg��31�600�272�950�431��32�600�272�950�431��33�600�272�950�431��41�700�317�1090�494��42�700�317�1090�494��43�700�317�1090�494��45�1200�544�1400�635��46�1200�544�1400�635��47�1200�544�1400�635��51�800�363�1100�499��52�800�363�1100�499��53�800�363�1100�499��55�1420�644�1420�644��56�1420�644�1420�644��57�1420�644�1420�644��



















































Table � SEQ Table \* ARABIC �3� - Economizer Refrigerant Charge

Economizer *�����Length (��Refrigerant (R-134a)���ft�m�lbs�kg��12�3.66�610�277��17�5.18�840�381��















Note:	* - 	Economizer refrigerant charges did not change.

		( -	Cooler Sizes 31-44 use the 12’ economizer.  Cooler sizes 48-48 use the 17’ economizer.



�







 



 










