Purpose: 





This bulletin is provide to advise the field of a product change, the


implementation of the slide valve shelf extension.





The slide valve shelf extension will provide more support at low load.





Machines Affected:





23XL frame 4 chillers having D40, D41, D60 and D61 compressors built after week ending 4197 (S/N 4197J-----) having D series compressor with compressor serial number 3897V02382 and higher that have a slide valve shelf extension.





Information:





The shelf extension is not retrofitable to existing D series compressors. The shelf must not be removed from rotor casing for alignment reasons.





Recommendation:





For D series compressor without relief shelf it is recommended that a slide valve clamp be installed during overhaul of the slide valve assembly.





Parts:





Slide Valve Clamp is available from RCD in the kit package only. The part number for the kit which includes clamp, drills, tap, bolts and instructions is 23XL660021.


























�

















�








		Slide Valve with Clamp


C9804 - 23XL Slide Valve Support �
�
Page 2�
�
�
�
�
�






23XL Slide Valve Support �
�
C9804�
�
�
�
1/30/98�
�
�
�
New�
�
�
23XL with D series compressors�
�
�
�






File:  Compressor-Motor-Gear-Drive�
�
�
�
�
�
�
�
�
Nick Chashin�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.46A, 2.40M, 5.25G�
�












