


Purpose:





To inform the field of a modification to the bearing system of the 17M,P,S compressor internal oil pump.








Background:





Several reports have been received from the field of bearing failures of the 17MA41�423 internal oil pump operating on R-134a.  As a result Engineering has redesigned the oil pump to use needle bearings.  The original bearings in the internal, shaft-driven internal oil pump, 17MA41�423 are sleeve type bearings which depend on surface film lubrication.  The chlorine in the refrigerant had acted as a high pressure surface lubricant and played a significant role in lubricating the pump.  The introduction of chlorine-free refrigerants has resulted in oil pump failures in these compressors because of the lack of that extra lubrication.  Only a few jobs have had failures but on those jobs the conditions are right to cause the pump to fail repeatedly.





The replacement for the 17MA41-423 pump has been used in production since December 1997 and is in stock under part number 17MA41-794.





If you are installing a pump in a chlorine based refrigerant, i.e. R-12, R-22, etc., compressor, the original pump 17MA41-423 will work.  If you are performing a refrigerant conversion to R-134a, the 17MA41-794 pump should be installed.


 


The new pump 17MA41-794 can be substituted in all cases for the original pump.





The 17M52-323 pump used on older 17M30 and 17P30 compressors is also designed with sleeve bearings.  Engineering is currently working on redesigning this pump.  Until a new pump is released for the 17M52-323, its use with R-134a should be restricted.


17M,P,S Oil Pump with R-134a�
�
C9806�
�
�
�
4/20/98�
�
�
�
New�
�
�
17M,P,S Compressors�
�
�
�






File:  Specified Parts�
�
�
�
�
�
�
�
�
Ted Libera�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�












