Purpose:





To inform the field of a field service technique and service parts for the 17FA111-1313, Neles-Jamesbury 2-4C-2236TT-1, 2” Reduced Port Ball Valve used with Hot Gas Bypass.








Information:





The Neles-Jamesbury Series 4000 ball valves use a metal ring to seal the valve body to the end cap.  This ring is a 316 stainless steel/graphite spiral-wound seal.  If for any reason, the valve body must be disassembled, a new seal must be used to insure a leak-tight joint. 





The Neles-Jamesbury seal part number for the 17FA111-1313 ball valve is JB004�0605-36.





These seals are hard to find and RCD does not stock them.  The best place to start is to call Neles-Jamesbury direct at (508)852-0200 and ask for the closest stocking distributor.





Our thanks to Ralph Galliford for bring this issue and solution to our attention.


17FA111-1313 Hot Gas Bypass Valve Assembly�
�
C9808�
�
�
�
4/22/98�
�
�
�
New�
�
�
17/19FA, 19EF�
�
N/A�
�






File:  Specified Parts�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�












