Purpose:

�


This bulletin is to inform the field of an RCD Product Integrated Control (PIC) Retrofit kit for R-134a systems, to upgrade older control systems to CCN compatible controls.  This kit was designed for comfort cooling applications only.  For machines in use in non-comfort cooling applications, contact the area/regional operations/service engineers for assistance.



Information:



RCD has set-up two separate packages for conversions to PIC controls from any control system.  
If the compressor sump is vented to the cooler, such that the 
oil 
sump is at cooler pressure, 
use the hermetic conversion kit. 
 
If this is not the case, the 
open-drive
 retrofit kit will be required. 
The 
hermetic conversion kit, 
19EX660003
 has all of the required items to convert a machine similar to the current 19EX.  
The 
open-drive conversion kit, 
17EX660001 
has all of the required items to convert a machine similar to the current 17EX. 
 
The control system logic operates for machines using R-134a only.


Part Number�Description�17EX660001�19EX660003��HF26BB025�Actuator Motor�1�1��HH79NZ047�Temperature Sensor�6�6��HK05YZ002�Pressure Transducer�4�3��HH79NZ073�Thrust Sensor�1�1��19EX04002601�High Pressure Switch�1�1��AT-225�Temperature Sensor Well�4�4��17EX54001702�PIC Control Panel�1�-��19EX54005002�PIC Control Panel�-�1��19EX54000302�PIC Power Panel�1�-��19EX04000202�PIC Power Panel�-�1��E950705-2�
PIC Sta
r
ter Conversion Panel w
ith 
SMM 
�1�1��06DA403844�Valve Assembly�5�4��32MP500354�Motor Sensor�-�2��17/19-1SI�Installation, Service, Operation & Maintenance Instructions�1�1��
The above list
 assumes the original control panel is a 32SM.  If the original control panel is a 32MP, the motor (32MP500354) and thrust bearing sensor (HH79NZ073) are not required.  



Additional Items required:

Job/machine “as built” wiring diagrams including chiller and starter data from the local Carrier Office

Electric drill, bits, and taps for installing sensors

Standard refrigeration tools

Touch-up paint, as required



The following hardware is required for mounting the inlet guide vane actuator:

(3) 1/4-20 x 1-3/4 long hex head bolts (use longer ones if required.)

(6) 1/4-20 hex nuts

(3)  1/4” washers

bushings, if needed



In addition to the above list, the inlet guide vane actuator linkage must be determined based on the application.  The guide vane actuator converts a 4 to 20 mA signal sent by the PSIO to a rotational position.  Full rotation of the actuator is 308 degrees.  It has a rated torque value of 400 in-lbs. (45.1 N-m) at 103.5 VAC.  



The 
PIC Starter Conversion Panel with the 
SMM 
is a separate enclosure to convert the existing starter to the current Z�375 specification.  The panel can be mounted inside, if space is available or outside of the starter.  The panel enclosure currently measures 24.38 x 20.38 x 6.75 inches (619 x 518 x 171 mm).  It is supplied with its own power supply and pilot relays.





In some cases, the oil pump overloads in older machines 
are
 in the 115 volt control circuit
.  I
f this is the case, 
use the 
cont
actor 2C 
in the power panel
 as a pilot relay
.  
Wire one of the terminals of the contactor in series with the overloads
 and oil pump contactor, M3
 in the existing 
oil
 pump 
contactor coil circuit.  This will keep the overloads in the circuit.




�
 
EMBED 
PBrush 
 
�
�
�





The PIC Retrofit kit is currently available through RCD.  Contact your RCD Order Correspondent for price information.







RCD PIC R-134a Retrofit Kit��C
9
810
����
04/
27
/98
����New���17/19 Series with R-134a w
ithout
 PIC Controls��N/A��






File:  Controls, Wiring���������Tom Pietrowicz���Alan M. Johnson������Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D,
 
2.40L, 
2.40M, 
2.44, 
2.4
6A
, 5.25C, 5.25G��






� REF number \* MERGEFORMAT �
C
9
810
� - � REF title \* MERGEFORMAT �
RCD PIC R-134a Retrofit Kit
�

Page � PAGE �
2
�





� REF number \* MERGEFORMAT �
C
9
810
� - � REF title \* MERGEFORMAT �
RCD PIC R-134a Retrofit Kit
�

Page � PAGE �2�










