Purpose:





To inform the field of a wiring scheme different that the “standard” PIC SIO bus between the PSIO and the CCM (Chiller Control Module).  This wiring applies to the PIC controls with a PSIO module only.





Information:





Several machines have been reported as having “Protective Limit - Diffuser Position Fault” problems at start-up.  The communication light (Green LED) is not lit with power on the control (Red LED blinking).  The wiring between the PSIO and CCM was found to be incorrect.  The wiring shown on the wiring diagram mounted on the machine is correct.  The CCM does not follow “normal” SIO convention.  On the PSIO (COMM3), J8-1 is positive and J8-3 is negative.  On the CCM, J7-1 is negative and J7-3 is positive.  The PSIO to CCM SIO bus should be wired as shown below.





� EMBED PBrush  ���


19XR Certified Prints for the Frame 7 Heat Exchanger, Catalog Number 581-969, Drawing Number: 19XR-271-C2, dated:  04/01/97 and Frame 8 Heat Exchanger, Catalog Number 581-970, Drawing Number: 19XR-281-C2, dated:  04/01/97, are both incorrect.  Please make a note of it. 





If the wiring is correct and the problem persists, check the DIP switch settings for the CCM.  They should be as follows:


Switch No.�
1�
2�
3�
4�
5�
6�
7�
8�
�
Postion�
ON�
ON�
ON�
ON�
OFF�
ON�
OFF�
ON�
�



PSIO to CCM Wiring�
�
C9814�
�
�
�
6/1/98�
�
�
�
New�
�
�
19XR with 02XR5 Compressor�
�
N/A�
�






File:  Controls & Wiring�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40L, 2.40M, 2.44, 2.46A, 5.25C, 5.25G�
�












