

BULLETIN

Carrier Corporation


North American Operations



Number:
C9815
Date:
06/01/98
Supersedes:
New
Date:
N/A

Title:
19XR/XRT Impeller Spacing Procedure

Category:
GENERAL
Termination Date:


Author:
Tom Pietrowicz



Dept:
CSS Service Engineering





Models Affected:
CAC:  19XR Frame 3 and 4

BDP:  




Purpose:
This bulletin describes the correct impeller spacing procedure and clearance for the 19XR and 19XRT compressors.

Information:
The 19XR impeller spacing procedure is very similar to that of the 19XL, but there are important differences outlined below along with the correct spacing for each individual compressor build.

The clearance dimension is dependent on the compressor frame size regardless of whether an energy recovery turbine is installed or not.  The frame size information is found in the unit model number.  The tenth position indicates the compressor frame size, and the twelfth position denotes the diameter of the impeller.

Position

1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18

1
9
X
R
-
3
7
3
7
3
2
2
C
D
H
6
3
-


Positions 1-4:  
19XR - Evergreen Centrifugal Chiller


Position   5:  

Turbine Designation


Positions 6-7:  
Cooler Code


Positions 8-9:  
Condenser Code


Position  10:

Compressor Frame


Position  11:

Impeller Shroud Code


Position  12:

Impeller Diameter Code


Position  13-14:
Motor Code


Position  15:

Motor Efficiency


Position  16-17:
Voltage Code


Position  18:

Special Order Code

Figure 1 - 19XR Model Code Designation

The impeller blades are relieved slightly from the shroud contour at the discharge tips requiring a “spacer tool” (shim stock) to be used to allow the impeller to sit squarely in the shroud while the impeller shim thickness is determined. 

Table 2 correlates the compressor frame size and diameter code with the three significant measurements needed to properly space and check during the assembly procedure.

The spacer (shown in Figure 4) must be held firmly against the slinger and then the thrust bearing housing, in order to obtain the proper measurements.  The following list of tools are not required tools, however shim calculation measurements are easier with the use of these tools:

Table 1 - Impeller Clamping Tool Usage




Used on

Tool No.
Description
Qty
02XR2
02XR/XRT3
02XR4
02XR5

TS-425
Clamp Fixture
1
X




TS-426
Clamp Fixture
1

X



TS-427
Clamp Fixture
1


X


TS-428
Clamp Fixture
1



X

Procedure:
1. Set the shroud on a flat surface as shown in Figure 3.

2. From Table 2 using the frame size and diameter code, determine the “spacer tool” thickness.

3. Obtain three small sections of shim stock of the thickness found in step 2.

4. Place the impeller into the shroud with the blades of the impeller supported by the shim stock.  Place the shim stock approximately 120° apart as close to the tip of the impeller as possible.  See Figure 3.

5. Gently move the impeller back and forth in the shroud to insure the impeller is not bottomed out in the shroud.  Do not rotate the blade in the shroud; damage to the impeller will result.

6. Using a precision straight edge lying across the back of the impeller, measure from the top side of the straight edge to the shroud mounting surface.  Do this in several places and take the average as the Dimension “A”.  This is worksheet Dimension “A” on Figure 3.

7. Measure from the top side of the straight edge to the hub counter bore.  Again, measure this in several places and take the average as the Dimension “B”.  This is worksheet Dimension “B” on Figure 3.

8. Subtract “B” from “A”, and enter the result in the “A - B” space provided.

9. Install the clamp fixture, if available, tightening the bolt to 25 ft-lbs (33.9 N-m).  Using a precision straight edge across the face of the diffuser, measure from the outer surface of the straight edge to the surface of the spacer.  Again, measure this in several places and take the average as the Dimension “C”.  This measurement should be taken while the shaft is held firmly in the counter-thrust position.  This is worksheet Dimension “C” on Figure 4.

10. Subtract the thickness of the straight edge, Dimension “E” from Dimension “C” and enter it on the worksheet for Dimension “D”.

11. Subtract “A - B” from Dimension “D”.  This is the total hub to spacer ring clearance in the counter-thrust position.  Enter the dimension on the worksheet.

12. Subtract the measured thrust clearance.

13. From Table 2 using the frame size and diameter code, determine the desired impeller clearance.  Enter this value on the worksheet.

14. Determine the shim thickness by subtracting the result from step 13 from the value found in step 12.

15. Complete the installation of the impeller and shroud.  When installing the impeller, Do not heat the impeller over 275 °F (135 °C);  damage to the impeller will result.  Heat the 02XR2-02XR4 impellers uniformly.  Heat the 02XR5 impeller bore only.  Heating more than the bore of the 02XR5 impeller will cause the impeller to interfere with the labyrinth.  Apply Loctite Removable Threadlocker 242 to the impeller retaining bolt and tighten to:

02XR2
02XR/XRT3
02XR4
02XR5

44 - 50 ft-lb

(59.6 - 67.8 N-m)
55 - 65 ft-lb

(74.5 - 88.1 N-m)
55 - 65 ft-lb

(74.5 - 88.1 N-m)
160 - 180 ft-lb

(217 - 244 N-m)

16. Determine the impeller eye clearance from Table 2 using the compressor frame size.

17. Measure the radial impeller eye clearance as shown in Figure 2 in four equally spaced places at the impeller eye.  This value should fall in the range of the specified values, listed in Table 2.

18. Complete the installation.

[image: image1.png]N

J|
A\
—

Clearance

| %A‘\ i'

(Radial)
\ \
p——

I =

NN

= .
N\PZP\NNN\\+





Figure 2 - Impeller Eye Clearance

Table 2 - Impeller Clearances



Spacer Tool
Impeller Eye


Compressor
Diameter
(Shim Stock)
Clearance
Impeller Clearance

Frame
Code
Thickness
(Radial)



9
0.003 (0.076)




8
0.002 (0.051)




7
0.002 (0.051)




6
0.001 (0.025)



2
5
0.001 (0.025)
0.011 - 0.021
0.019


4
0.001 (0.025)
(0.279 - 0.533)
(0.483)


3
0.001 (0.025)




2
0.001 (0.025)




1
0.001 (0.025)




9
0.012 (0.304)




8
0.011 (0.279)




7
0.009 (0.229)




6
0.008 (0.203)



3
5
0.008 (0.203)
0.010 - 0.024
0.024


4
0.007 (0.178)
(0.254 - 0.610)
(0.610)


3
0.007 (0.178)




2
0.006 (0.152)




1
0.006 (0.152)




9
0.011 (0.279)




8
0.010 (0.254)




7
0.010 (0.254)




6
0.007 (0.178)



4
5
0.005 (0.127)
0.015 - 0.029
0.030


4
0.005 (0.127)
(0.381 - 0.737)
(0.762)


3
0.004 (0.102)




2
0.004 (0.102)




1
0.004 (0.102)




9
0.009 (0.229)




8
0.008 (0.203)




7
0.007 (0.178)




6
0.006 (0.152)



5
5
0.005 (0.127)
0.023 - 0.037
0.043


4
0.004 (0.102)
(0.584 - 0.940)
(1.092)


3
0.003 (0.076)




2
0.002 (0.051)




1
0.001 (0.025)



Note:
All dimensions in inches.  Dimensions shown in () are in mm.

IMPELLER SPACING

(Shim Sizing)

MEASUREMENTS TO BE TAKEN WITH THE IMPELLER SHAFT

IN COUNTER-THRUST POSITION

Description
Dimension
Value

Straight Edge to Shroud Flange


“A”


Straight Edge to Hub Counter Bore


“B”


Hub to Flange

  (calculated)
“A” - “B”


Diffuser to Spacer Ring (Top of Straight Edge)


“C”


Thickness of the Straight Edge


“E”


Diffuser to Spacer Ring

  (calculated)
“C” - “E” = “D”


Hub to Flange

  (calculated)
“A” - “B”


Total Clearance (Impeller to Spacer Ring)

  (calculated)
“D” - (“A” - “B”)


Subtract Measured Thrust Clearance





Subtract Impeller Clearance (From Table 2)





Shim Thickness Required





[image: image2.png]IS

I 0

7
)

9 | mm\

\
\

7

N
M

"

Y

A

~




Figure 3 - Impeller/Shroud Dimensions

[image: image3.png]PIPE DIFFUSER

\STRAIGHT EDGE

\,\m
F

SPACER

\\w

CLAMPING
FIXTURE

%,

IMPELLER SHAFT
<4— COUNTER-THRUST DIRECTION




Figure 4 - Impeller Depth Dimensions
Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















