�
Purpose:





To inform the field of a correction to the 02XR2 impeller interference dimension and a change to the 02XR5 interference dimension listed in the Start-Up, Operation and Maintenance Instructions, 19XR-2SS. 








Information:





The 02XR2 impeller interference, dimension “E” on page 92, is incorrectly stated as a clearance.  The dimension should be -0.0020/-0.0005 (-0.0508/-0.0127 mm).





The 02XR5 impeller interference fit has been changed by engineering.  Compressors produced after July 13, 1998 (week 29) will have the new interference dimension.  Replacement impellers shipped from RCD will have the new interference dimension shortly.  The old interference dimension was incorrectly stated as a clearance in the Start-Up, Operation and Maintenance Instructions as 0.0031/0.0017 (0.0787/0.0432 mm).  The new dimension “E” for the 02XR5 compressors on page 92 is �0.0019/�0.0005 (�0.0483/�0.0127 mm).





Please make a note of these changes.





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �02XR2 and 02XR5 Impeller Interference Corrections �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9816  �





AUTHOR:  � REF author \* MERGEFORMAT �Tom Pietrowicz�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �19XR �


	KEY WORDS:	COMPRESSR, MAINT, SERVPARTS





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9816  � - � REF title \* MERGEFORMAT �02XR2 and 02XR5 Impeller Interference Corrections �


Page � PAGE �1�








02XR2 and 02XR5 Impeller Interference Corrections �
�
C9816  �
�
�
�
06/10/98�
�
�
�
New�
�
�
19XR �
�
N/A�
�






File:  Compressor, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9816  � - � REF title \* MERGEFORMAT �02XR2 and 02XR5 Impeller Interference Corrections �


Page � PAGE �1�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























