�
Purpose:





To inform the field of a potential problem with the 06DA403844 Schrader Valve Assembly.  This 
assembly
 consists of a brass body and 
Schrader
 valve
 core
.



Information:





There have been sporadic reports from the field of non-communicating pressure transducers or pressure switches with 
a
 refrigerant or oil environment.  The problem has been traced to the Schrader Valve Assembly, 06DA403844.  In some cases, the assembly’s schrader core is not 
depressed 
enough 
by the pressure sensing device 
t
o open a path to the 
pressure
 environment.  As a result
,
 the pressure sensing device 
can
not read the 
pressure at that point in the system.



If this case is discovered, 
use the following procedure to 
alleviate the problem without changing ou
t
 the 
complete 
valve assembly
.



The core is threaded into the body with 0.206-36 thread
s
 (36 threads/inch).  In order for the pressure device to communicate with the environment, the schrader valve 
core 
may need to be moved 
such that the valve core extends past the end
 
of
 the valve assembly body.  
See 
�
 
REF 
_Ref422044930 \* MERGEFORMAT
 
�
Figure 
1
�
.  
To accomplish this safely, use the Schrader Valve Core Removal Tool described in Service Bulletin C9405.  Ideally, the core should not be any
 
more than 0.010 inches (0.254 mm) outside of the valve assembly as shown in 
�
 
REF 
_Ref422044930 \* MERGEFORMAT
 
�
Figure 
1
�
.  If the pressure device is not communicating with the environment intended, back the core out until the device can depress the core and communicate with the environment.  Use the tool specified 
in Service Bulletin C9405 
to back 
the core
 out.  P
ay 
careful 
attention to the safety warnings listed about the tool.





�
 
EMBED 
PBrush 
 
�
�
�



Figure 
�
 
SEQ 
Figure \* ARABIC
 
�
1
�
 - S
chrader Valve Assembly Dimensions






If the 
valve 
core leaks before communication is established, the valve assembly, 06DA403844 must be replaced.








�SERVICE BULLETIN DISTRIBUTION



BULLETIN NAME:  � REF title \* MERGEFORMAT �
06DA403844 Schrader Valve Assembly  
�



BULLETIN NUMBER:  � REF number \* MERGEFORMAT �
C98
18
 
�



AUTHOR:  � REF author \* MERGEFORMAT �
Tom
 
Pietrowicz
�



COLLS:

	MODEL CODE:	� REF units \* MERGEFORMAT �
17EX/FA, 19EF/FA/EX/XL/XR/XRT/XT, 
23XL
�

	
KEY WORDS:	CONTROLS, REFRIGERNT, OPERATN




��Mail Key�COIN�cc:Mail��X�DOMESTIC SERVICE PERSONNEL

   BSS Regional Operations Managers

   BSS Area Managers

   BSS account Executives

   BSS Technical Consultants

   BSS Service Offices

   BSS Regional General Managers

   BSS Service Managers and Mechanics�

2.40A

2.40B

2.40D

2.40M

-

2.40

2.46A�

#BSS-ROM

-

-

#CBSTSE

#BSSSVC

#BSS-RGM

-���X�INTERNATIONAL SERVICE PERSONNEL

   International Service Managers

   Miscellaneous Service Personnel�

5.25G

2.33A�

#SBMISC

#SBMISC����DOMESTIC SALES PERSONNEL

   Canadian Field Sales

   BSS/ESS Sales/Managers



(Service Bulletins which relate to application)�

2.44

2.40L�

#CSD-CND

#BSSESS����INTERNATIONAL SALES PERSONNEL

   International Marketing Managers



(Service Bulletins which relate to application)�

5.25C�

#CIC-ASC���X�SPECIAL DISTRIBUTION

   CAES Products, Service & SO Engineers

   Miscellaneous Eng, Mktg, RCD Personnel�

2.33B

2.33D�

#SBMISC���



� REF number \* MERGEFORMAT �
C98
18
 
� - � REF title \* MERGEFORMAT �
06DA403844 Schrader Valve Assembly  
�

Page � PAGE �
1
�







06DA403844 Schrader Valve Assembly  ��C98
18
 ����06/
10
/98����New���17EX/FA, 19EF/FA/EX/XL/XR/XRT/XT, 
23XL��N/A��






File:  Controls & Wiring���������Tom Pietrowicz���Alan M. Johnson������Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G��






� REF number \* MERGEFORMAT �
C98
18
 
� - � REF title \* MERGEFORMAT �
06DA403844 Schrader Valve Assembly  
�

Page � PAGE �
2
�







Title��Number����Date����S/S�����Date��



File:  ���������Tom Pietrowicz���Alan M. Johnson������Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G��


















