�
Purpose:


To inform the field of changes to the pumpout control box wiring for control boxes 19EA41-588 and 19EA42-588.  These control boxes are used on the 19EA Pumpout Units.  The 19EA pumpout units were sold as a factory installed option on most high pressure machines, through RCD as Service Pumpout Units, and installed on 19XB storage vessels.








Information:


Engineering has added a wire (Item 15) to connect the High Pressure Switch to Terminal 5 in the 19EA41-588 and 19EA42-588 control boxes, as shown below.





� EMBED PBrush  ���





This wire is required for the proper operation of the high pressure switch on 17/19EX/FA, 19XL/XR/XRT/XT and Service Pumpout units.





Pumpout units produced between late 1994 and mid 1996 were missing the wire (Item 15).  If a jumper between terminals 3 and 5 was installed instead of the wire from Terminal 5 to the High Pressure Switch, the pumpout unit will operate with the High Pressure Switch disabled.  When performing routine maintenance check the pumpout unit to be sure that the High Pressure Switch is properly wired into the circuit.





The additional wire (Item 15) is not required in the 19XB storage vessels since the High Pressure Switch connects in series with the High Level Safety Switch.  If the wire is present, it should be removed.





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �19EA Pumpout Control Box Wiring Changes  �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9820�





AUTHOR:  � REF author \* MERGEFORMAT �Tom Pietrowicz�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �17, 19, 23 with Pumpout Units �


	KEY WORDS:	PUMPOUT, PURGE





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9820� - � REF title \* MERGEFORMAT �19EA Pumpout Control Box Wiring Changes  �


Page � PAGE �1�








19EA Pumpout Control Box Wiring Changes  �
�
C9820 �
�
�
�
06/29/98�
�
�
�
New�
�
�
17, 19, 23 with Pumpout Units �
�
N/A�
�






File:  Purge, Pumpout�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9820� - � REF title \* MERGEFORMAT �19EA Pumpout Control Box Wiring Changes  �


Page � PAGE �2�








Title�
�
