�
Purpose:





To inform the field of the procedure to measure the journal bearing clearance on the 17FA and 17FX externally geared compressors.  These compressors have tilting shoe journal bearings, that require a special measuring procedure to measure the diametrical clearance.





Information:





The shaft clearance on these bearings can be checked with a dial indicator at each pad pivot point.  The indicator should be zeroed with the shaft pushed toward the pivot point of the bearing.  The indicator should be read with the shaft pushed directly away from the pivot point.  The diametrical clearance is the indicator reading multiplied by 0.894.





This procedure should be repeated for each of the five pads.





� EMBED PBrush  ���


Figure � SEQ Figure \* ARABIC �1� - 17FX54001401 Cross Section  (Typical)





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �17FA/FX Journal Bearing Clearance Measurements  �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9821  �





AUTHOR:  � REF author \* MERGEFORMAT �Tom Pietrowicz�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �17FA/EX - with 17FA/FX Externally Geared Compressors  �


	KEY WORDS:	COMPRESSR, MAINT





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9821  � - � REF title \* MERGEFORMAT �17FA/FX Journal Bearing Clearance Measurements  �


Page � PAGE �3�








17FA/FX Journal Bearing Clearance Measurements  �
�
C9821  �
�
�
�
07/06/98�
�
�
�
New�
�
�
17FA/EX - with 17FA/FX Externally Geared Compressors  �
�
N/A�
�






File:  Compressor, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9821  � - � REF title \* MERGEFORMAT �17FA/FX Journal Bearing Clearance Measurements  �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























