�
Purpose:





To inform the field of a leak path repair for the Pall Oil Filter casings.








Information:





In some cases, the Pall oil filter casings (KH18MB003) on 23XL machines with D40, D41, D60 and D61 compressors, develop minor oil leaks around the o-ring joint.  This situation has been traced to a stretched o-ring.  Pall has recommended using a larger o-ring in place of the current one to stop the leaks.  This solution has been tried on several job sites and has worked. The new o-ring, KK71EW154 is slightly larger than the old one and is included in the filter replacement kits, 23XL660016.  The new o-ring is available in RCD.





�
Carrier Part No.�
Standard ID, in. (mm)�
Standard Width, in. (mm)�
�
Old O-ring�
KK71EW153�
3.487 (88.6)�
0.103 (2.6)�
�
New O-ring�
KK71EW154�
3.737 (94.9)�
0.103 (2.6)�
�



RCD stock of the 23XL660016 kit has been reworked.  New machines will be modified from the factory once the new o-ring material is available.





Our thanks to Phil Carnegie for bringing this solution to our attention.








�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �23XL Oil Filter Casing Leaks  �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9825  �





AUTHOR:  � REF author \* MERGEFORMAT �Benny DiMarco�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �23XL with D Series Compressors  �


	KEY WORDS:	LUBE, SERVPARTS





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9825  � - � REF title \* MERGEFORMAT �23XL Oil Filter Casing Leaks  �


Page � PAGE �3�








23XL Oil Filter Casing Leaks  �
�
C9825  �
�
�
�
10/27/98�
�
�
�
New�
�
�
23XL with D Series Compressors  �
�
N/A�
�






File:  Specified Parts�
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9825  � - � REF title \* MERGEFORMAT �23XL Oil Filter Casing Leaks  �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























