�
Purpose:


To advise the field of a solution to intermittent problem of recognizing water flow through a vessel in a low pressure drop applications.








Information:





Information received back from the field indicates that the pressure switch used to sense water flow part number HK06ZC033 in low pressure drop applications may be responsible for intermittant nuisance trips.





The current switch which is manufactured by United Electric Controls is factory set to make at 2 PSID and break at 1 PSID. These settings can be adjusted in the field at the time in which the chiller is being started by using controls test and adjusting the switch until the make is recognized by the PIC controls. In most applications these switches are adequate. On a single pass machines with pressure drops below 2 PSID the switch can sometimes give the false indication that no flow is present preventing the chiller from starting.





.





Action:


If nuisance problems occur with the pressure differential switch a more sensitive switch is available from W.E. Anderson. The part number of the switch H3A-2SCMV.


The operating range is .5 to 15 PSID and is rated at 1500 PSI. The contacts on this switch are gold and rated at 1 amp at 125 VAC and .5 amp inductive and 1 amp resistive at 30VDC. The switch can be purchased through RCD under part number HK06ZC001.








�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:Water Flow Pressure Switches 





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C982�6





AUTHOR:  Benny DiMarco





COLLS:


	MODEL CODE:	17, 19 and 23 Series


	KEY WORDS:	Pressure Switch





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�









� REF number \* MERGEFORMAT �C982� - � REF title \* MERGEFORMAT �Water Flow Pressure Switches  �


Page � PAGE �1�




















Water Flow Pressure Switches  �
�
C9826�
�
�
�
10/9/98�
�
�
�
New�
�
�
17,19 and 23 Series Chillers�
�
N/A�
�






File:  Installation, Start-Up & Operation�
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C982� - � REF title \* MERGEFORMAT �Water Flow Pressure Switches  �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























