�
Purpose:





To define 23XL capacity slide rod surface finish requirements.





Reference:


	Bulletin C9803 - Slide Valve Rework Procedure;


		Fixed VI Compressors; Page 2; Sect. II, Step #9


		Variable VI Compressors; Page 7; Sect II, Step #13 





Background:


Seal ring life is directly affected by the contact area surface finish of the capacity slide rod.  Testing has shown that a slide rod surface finish of .55 micro-meters/22 micro-inches, or better, is the required finish for optimized seal life.





Requirement:


If a seal ring is worn, measure the slide rod surface finish in the seal ring contact area listed below for the particular frame size compressor you are servicing.  The surface finish in the designated areas must be .55 micro-meters/22 micro-inches, or better.   If the surface finish exceeds this requirement, replace the slide rod or have the rod polished to the required finish at a machine shop.


� EMBED PBrush  ���


					Tons	    “F”


Compressor Frame:	C2	 160	188mm


				C4	 200	188mm


				C6	 250	205mm


				D4	 300	182mm


				D6	 350	210mm








�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �Capacity Slide Rod Surface Finish Requirements �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9827  �





AUTHOR:  � REF author \* MERGEFORMAT �Mike Grimshaw�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �23XL Compressors (All Frames)  �


	KEY WORDS:	COMPRESSR, SERVPARTS





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9827  � - � REF title \* MERGEFORMAT �Capacity Slide Rod Surface Finish Requirements �


Page � PAGE �3�








Capacity Slide Rod Surface Finish Requirements �
�
C9827  �
�
�
�
10/27/98�
�
�
�
New�
�
�
23XL Compressors (All Frames)  �
�
N/A�
�






File: Compressor, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Mike Grimshaw�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9827  � - � REF title \* MERGEFORMAT �Capacity Slide Rod Surface Finish Requirements �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























