�
Purpose:





To provide information to the field regarding tube failure analysis.





Information:





From time to time, tube samples are sent in from the field for analysis.  Many of the reports indicate an Eddy Current analysis showed some kind of defect with the tube.  Many times, the whole tube is sent in with only a small defect in the center of the tube, and no indication of where it is. To speed up the analysis, only a small section of tube needs to be sent in, approximately 36 inches (1.0 m) of tube with the defect identified and in the middle of the tube.  With each sample indicate the following:





The complete model and serial number of the machine


The location in the tube bundle, row and column , a drawing is helpful


The location in the axial direction of the vessel, bay number with a reference to the drive or compressor end for centrifugals.  For the absorption machines, The location in the axial direction of the vessel, bay number with a reference to the right or left side facing the control panel


Mark the area of the defect in the tube


A water sample is not required, but may reveal a clue in the analysis of the failure





All of these items should help to the response time for the tube analysis.





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �Tube Failure Analysis  �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9828�





AUTHOR:  � REF author \* MERGEFORMAT �Tom Pietrowicz�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �16, 17, 19, and 23 Series  �


	KEY WORDS:	HEATEXCH 





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9828� - � REF title \* MERGEFORMAT �Tube Failure Analysis  �


Page � PAGE �3�








Tube Failure Analysis  �
�
C9828�
�
�
�
10/29/98�
�
�
�
New�
�
�
16, 17, 19, and 23 Series  �
�
N/A�
�






File:   Absorption:  Tubes and Retubing


          Centrifugal:  Cooler, Condenser, Economizer�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9828� - � REF title \* MERGEFORMAT �Tube Failure Analysis  �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























