�
PURPOSE:	





To inform of an alternate method of controlling the condensing pressure in the purge pot of PreVent purges.  This method replaces the existing regulating valve part number EB51GD061. 





BACKGROUND:  





The regulating valve works in most cases but may not function reliably in some applications.  If a regulating valve becomes inoperable, it may be replaced with the existing valve or the following change can be made to offer better reliability.





INSTRUCTIONS:  





Remove the existing regulating valve and in its place pipe in a solenoid valve, (S5), part number EF13CQ064, a tee to accept a ¼” tube between the valve and the purge pot, and a 1/8” flare bonnet orifice on either side of the valve. (See Figures 1, 2, 3 and 4) Use the Carrier solenoid because it is qualified for use in a PreVent purge.  Mount a pressure switch, part number HK01CW010, in a suitable location.   Pipe the pressure capillary from this switch to the ¼” tee installed above. 





Wire the pressure switch and solenoid in series between L1 and L2 power.  Properly ground the switch and solenoid.  (See Figure 5.)





Refer to the drawings and schematics attached.�












� EMBED PBrush  ���


FIGURE 1 


(Flow Schematic)





� EMBED PBrush  ���





FIGURE 2  


(End View)





� EMBED PBrush  ���








FIGURE 3  


(Side View)











� EMBED PBrush  ���








FIGURE 4  


(Top View)





� EMBED PBrush  ���


FIGURE 5  


(Electrical Schematic)


�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  � REF title \* MERGEFORMAT �PreVent Regulating Valve   �





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9830 �





AUTHOR:  � REF author \* MERGEFORMAT �Richard L Martin�





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �Low Pressure�


	KEY WORDS:	





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9830 � - � REF title \* MERGEFORMAT �PreVent Regulating Valve   �


Page � PAGE �7�








PreVent Regulating Valve   �
�
C9830 �
�
�
�
11/06/98�
�
�
�
None�
�
�
Low Pressure Chillers�
�
 �
�






File:  Purge Pumpout�
�
�
�
�
�
�
�
�
Richard L Martin�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9830 � - � REF title \* MERGEFORMAT �PreVent Regulating Valve   �


Page � PAGE �4�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























