�
Purpose:





To inform the field of a new Product Integrated Control system (PIC) for the 19XR/XRT product line.





Information:





A new control system called PIC II (Product Integrated Control II) has been designed for the 19XR/XRT product line.  As of production week 28 (July 6, 1998) all 19XR chillers with compressor frame size 2 through 5 and 19XRT chillers with compressor frame size 3 have PIC II controls installed.  The PIC II controls are a major design upgrade to the existing PIC I (Product Integrated Control I) controls that have existed on the 19XR/XRT product line.








Familiarization:





The following Comparison Table is arranged to summarize the comparison between the new PIC II control and the older PIC I control.  The table on the left lists all the components in PIC I control and the table on the right lists all the components that replace the existing control with the new PIC II components.  A comparison will be provided for the following portions of the control system: Control Panel, Power Panel, Motor Starter, Machine Sensors/Actuators, and Machine Safeties.


�
COMPARISON TABLE


PIC I vs PIC II


(19XR/XRT chiller with Cutler-Hammer unit mounted starter)








	                 PIC I						     PIC II





CONTROL PANEL�
�
CONTROL PANEL�
�
( LID2B (Local Interface Device)�
�
�
�
( PSIOII-02 (Processor Sensor Input/Output Module)�
�



( CVC (Chiller Visual Controller)�
�
( 6 Pack Relay Board�
�
( CCM (Chiller Control Module)�
�
( Power Supply/ Comparator Board�
�
�
�
( 8 Input Options Module (1 & 2)�
�
�
�






	                 PIC I						     PIC II





POWER PANEL�
�
POWER PANEL�
�
( (3) 24 VAC control transformers�
�
( (2) 24 VAC control transformers�
�
( (1) 21 VAC control transformer�
�
( 1C oil heater contactor�
�
( Oil differential pressure switch�
�
( 2C oil pump contactor�
�
( 1C oil heater contactor�
�
( 3C HGBP relay (optional)�
�
( 2C oil pump contactor�
�
�
�
( 3C HGBP relay (optional)�
�
�
�
( 115/230 VAC selector switch�
�
�
�






	                 PIC I						     PIC II





MOTOR STARTER�
�
MOTOR STARTER�
�
( SMM (Starter Management Module)�
�
�
�
( IQ1000II Motor Protection System�
�
�
�
( IQDP4130 Digital Volt Meter (Optional)�
�
( ISM (Integrated Starter Module)�
�
( (5) pilot relays�
�
�
�
( T2 24 VAC transformer�
�
�
�
( T3 24 VAC transformer�
�
�
�
�
	                 PIC I						     PIC II





MACHINE SENSORS/ACTUATORS�
�
MACHINE SENSORS/ACTUATORS�
�
( (8) 5 k( thermistors�
�
( (8) 5 k( thermistors�
�
( (4) 5 VDC pressure transducers (refrigerant side)�
�
( (4) 5 VDC pressure transducers (refrigerant side) ((5) for frame 5 compressor)�
�
�
�
( (4) 5 VDC pressure transducers (waterside)�
�
( Inlet guide vane motor with 4-20 mA drive�
�
( Inlet guide vane motor with floating point drive and 0-3 VDC feedback�
�
( Diffuser actuator motor with 4-20 mA drive�
�
( Diffuser actuator motor with 4-20 mA drive�
�






	                 PIC I						     PIC II





MACHINE SAFETIES�
�
MACHINE SAFETIES�
�
( High discharge pressure cutout switch (pressure limiting device)�
�
( High discharge pressure cutout switch (pressure limiting device)�
�
( (2) Waterside differential pressure switches (flow switch)�
�
( No waterside differential pressure switches are required.  Water flow is sensed by pressure transducers (waterside flow devices) for flow/no flow confirmation.�
�
�
�
( HPR (High Pressure Relay) (contacts in series with 1CR).  Located in pressure limiting circuit driven off 2C auxiliary contact on the compressor oil pump contactor.�
�
�



�





PIC II CONTROL PANEL 


WITH CVC (CHILLER VISUAL CONTROLLER)








The CVC mounted in the control panel contains the following features:





( Visual display with integral back lighting (light shuts off after 15 minutes of inactivity)





( Programmable softkeys for selecting menus, and changing points





( Contains the software to control the chiller and stop operation due to safety trips





( Contains non-volatile memory (EPROM).  No battery back-up is required





( Connects to the CCN network (Carrier Comfort Network) and EMS systems (Energy Management)�









�





INTERNAL VIEW OF CONTROL PANEL


INCLUDING REAR VIEW OF CVC


� EMBED Word.Picture.6  ���





CCM


(CHILLER CONTROL MODULE)





























The CCM mounted in the control panel contains the following features:





( Monitors inputs from machine sensors which include thermistors for temperature sensing, pressure transducers, and inlet guide vane position feedback





( Includes termination points for optional temperature sensing, remote temperature reset, auto demand limit, auto chilled water reset, and refrigerant leak sensor





( Provides AC switching (through TRIACs) to directly control hot gas bypass, compressor oil pump, and compressor oil heater contacts including switching for floating point drive control of the guide vane actuator motor





( Provides a 4-20 mA output to control the split ring diffuser for the frame 5 compressor





�
�





ISM


(INTEGRATED STARTER MODULE)





The ISM mounted in all motor starter types except Benshaw Inc. solid state starters( contains the following features:





( Provides motor starting control, monitoring and motor protection reported to the CVC through RS485 communications on the SIO (Sensor Input Output) buss





( Provides protection for:





- 1M/2M contact faults				- High motor amps


- Starter acceleration fault				- Motor locked rotor trip


- Phase loss						- Starter lock rotor trip


- Single cycle dropout				- Phase reversal


- High line voltage					- Line frequency trip


- Low line voltage					- Voltage imbalance


- Power loss						- Current imbalance


- Starter fault (optional starter protective devices)


- Motor overload trip (I2T electronic motor overload)


- Ground fault protection, including phase to phase on low voltage units





( Convenient motor starter configuration and display of motor status at CVC in control panel which includes the display of:





- Line current on phase 1, 2, and 3		- Power factor


- Average line current				- Kilowatts


- Line voltage on phase 1, 2, and 3		- Kilowatt-Hours


- Average line voltage				- Line frequency


- Ground fault on all three phases (low voltage units only)


- Ground fault on phase 1 (for medium and high voltage units)


- I2T sum heat on phase 1, 2, and 3 (electronic motor overload)





(The REDISTART MICRO( control in the Benshaw Inc. solid state starter communicates directly to the CVC and provides all ISM functionality.  A separate ISM module is not used.  The software that normally resides in the ISM is now resident in the EPROM on the CPU card in the REDISTART MICRO( control.


Literature/Training material





The following is a list of literature and training material available for PIC II control and can be ordered through Literature Distribution:





Title							          Form Number	      Catalog Number





19XR/XRT Product Data					19XR-3PD		521-900


19XR Installation Instructions					19XR-3SI		531-973


19XR Start-up, Operation, and Maintenance Instructions		19XR-3SS		531-974





19XRT Installation Instructions					19XRT-2SI		531-976


19XRT Start-up, Operation, and Maintenance Instructions	19XRT-2SS		531-977





Prepared by the Bynum Training Center:


Program (Video/Slides/Book)					19XR/XRT-03		021-907


Book								19XR/XRT-04		021-908


CD-ROM Multimedia Trainer with audio and book		19XR/XRT-04CD	021-909





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  PIC II Controls Familiarization 





BULLETIN NUMBER:  C9831





AUTHOR:  Paul Holsinger





COLLS:


	MODEL CODE:	19XR/XRT


	KEY WORDS:	CONTROLS, STARTER, WIRING





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CSS Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT �Error! Reference source not found.�


Page � PAGE �3�








PIC II Controls Familiarization�
�
C9831�
�
�
�
12/10/98�
�
�
�
New�
�
�
19XR/XRT�
�
N/A�
�






File:  Controls, Starter, Wiring�
�
�
�
�
�
�
�
�
Paul A. Holsinger�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






C9831 - PIC II Controls Familiarization


Page � PAGE �3�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Paul A. Holsinger�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�



























