


�
Purpose:





To inform the field of an improved 23XL “Belleville type” spring washer which produces increased clamping force to the outer bearing race on “D” frame compressors.





Reference:


	Bulletins  C9803  23XL Slide Valve Rework Procedure


		     C9804  23XL Slide Valve Support





	Dimensions. 	.140” (3.56mm)


			.150” (3.8mm)


			.169” (4.3mm)


			.197” (5.0mm)





Background:


The outer bearing clamping force, applied by the deflection of the current production spring washer, is significantly influenced by the tolerance build-up of the outlet casing machining, bearings, spacer and spring washer.   When the combined tolerance build reduces washer deflection towards the minimum required, the spring washer on some D frame compressor male rotor bearing has rotated, wearing the spacer, washer and slide casing surface.





Information:


A new .169”(4.3mm) thick spring washer will be implemented as standard during 1999, replacing the current washer and providing a significant increase in clamping force to the outer rotor bearings on D frame 23XL compressors.    When the planned spring washer change is implemented, the standard washer and spacer will be available through RCD.





In the interim, Service Engineering has had a quantity of thicker .169”(4.3mm) spring washers produced for replacement of current spring washers that have been found to have spun on existing D frame compressors.    The new replacement .169”(4.3mm) spring washers have to be ordered through Service Engineering until the change is implemented as standard production.





When requesting a new .169”(4.3mm) spring washer, follow the retrofit procurement requirements by first obtaining the specified dimensions from your machine.





Retrofit Requirements: Requesting Branch 


1) Referring to the page 3 diagram, accurately measure the “A” (Outlet casing bolting 	surface to outer bearing race) depth dimension.


2) Accurately measure the spacer height dimension “B”.


3) Inspect the slide valve casing, in the spring washer contact area, for grooving due to 	washer rotation.   If grooving is present, measure depth of grooving as 	accurately as possible.


4) Provide these dimensions, unit model number, job name and machine serial 	number to Service Engineering, along with your request for a thicker 	.169”(4.3mm) spring washer.





Retrofit Requirements: Service Engineering


5) Calculate the existing Compressed Spring Washer Height - “C”   (C = A - B)


	Measureable slide casing grooving must be added to “C” for a final value.


6) Calculate the Optimized Spacer Height Required, dimension “O”, to obtain the 	targeted spring washer deflection of.140”(3.56mm).


	“O” = A - (Averaged washer free height - .140”(3.56mm))


7) Compare the calculated Optimized Spacer Height “O”, required to obtain the target 	spring deflection of.140”(3.56mm), to the Measured Spacer Height “B”.   If the 	existing spacer height dimension “B”, is within +/-.002”(.05mm) of “O”, the 	existing spacer may be used with the new spring washer.





		Optimized Spacer Height: “O”	=_______


		Measured Spacer Height “B”	=_______





8) If “O” is more than .005”(.13mm) greater than “B”, a new spacer must be machined to dimension “O”.   If “B” is more than .005”(.13mm) greater than “O”, then the existing spacer must be remachined to the “O” dimension.





Spring washer deflection limit check:


9) If a spring washer is deflected too far, it will bottom out and lose its clamping force.   	The limit for this application is 90% of available washer deflection.   Service 	Engineering will confirm that the targeted 140”(3.56mm) deflection does not 	exceed 90% of the available deflection height for the selected washer by the 	following procedure.


9a) The “averaged free height” of the selected washer is established by 	


averaging the 4 height measurements written on the face of 	the washer


received.


	9b) The “average deflectable height “Hd”” for the thicker spring washer will be 			determined by subtracting the .169”(4.3mm) washer thickness from the 			“averaged free height”.


	9b) Divide .140”(3.56mm) by the “Hd”value.   If the result is greater than .9, the 			selected spring washer cannot to be used.





Installation:


The interim .169”(4.3mm) washers from Service Engineering are machined from .197”(5.0mm) washers. To optimize the upgrade, a deflection of .140“(3.56mm) +/-.005”(.13mm) has been targeted.   If the old spacer will produce a spring deflection within .140”(3.56mm) +/-.005”(.13mm), and it has not been worn by rotation, it can be reused.   Otherwise, the new spacer must be machined to the specific requirements of the unit retrofit, determined from the prior calculation processes.   





When the standard change is made in 1999, special machining of the spacers is not expected since the pounds to deflection curve profile of stamped .169”(4.3mm) washers is more flat over a broader range of deflection.    If a spacer had worn due to rotation, it would be replaced with a standard replacement spacer obtained through RCD.


�











	


�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  Spring Washer Improvement





BULLETIN NUMBER:  C9833





AUTHOR:  Mike Grimshaw





COLLS:


	MODEL CODE: 23XL


	KEY WORDS: compressor, maint, servparts 





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT �Error! Reference source not found.�


Page � PAGE �3�








Spring Washer Improvement�
�
C9833�
�
�
�
12/10/98�
�
            �
�
New�
�
�
23XL “D” frame Compressors�
�
N/A�
�






File:  Compressor, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Mike Grimshaw�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






Spring Washer Improvement


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























