
19XR HIGH SPEED SHAFT CHANGE
C9718PRIVATE 


10/30/97













  NEW




19XR FRAME 3 AND 4

PURPOSE:

To inform the field of a change in the diameter of the high speed shafts on frame 3 and frame 4 19XR compressors.

GENERAL INFORMATION:

The initial release of the smaller capacity frame three and frame four 19XR compressors were released with a high speed shaft that measured 1.15 inches at the impeller mounting end of the shaft. As further testing was completed on larger tonnage frame three and four compressors it was found that the impeller could deflect during operation. To increase the overall strength of the shaft the diameter was changed to 1.37 inches. Approximately 8/97 all production units utilized the new large diameter shaft.

SERVICE PARTS

Service parts only stocks the new larger diameter shaft and associated impellers for frame three and frame four compressors. When ordering replacement parts it will be necessary to check the diameter of the shaft (see figure 1) before ordering the parts needed for the repair (i.e. if the machine has a small diameter shaft and either the shaft or impeller needs to be replaced, a new shaft, impeller spacer, and shim pack, etc. will need to be ordered).

Figure 1. High Speed Shaft

The table below outlines the large diameter high speed assembly part numbers along with the other associated parts that will need to be ordered if replacing a small diameter with a large diameter. The large diameter shaft will work with a small diameter thrust housing assembly.

PART NAME
FRAME 3 COMPRESSOR
FRAME 4 COMPRESSOR 

HI SPD BRG & SHAFT ASSY 60 HZ
02XR34000201
02XR44000701

HI SPD BRG & SHAFT ASSY 50 HZ
02XR34000202
02XR44000702  *

HIGH SPEED SHAFT 60 HZ
02XR35008401
02XR45008601

HIGH SPEED SHAFT 50 HZ
02XR35008402
02XR45008602

SPACER
02XB35006801  *
02XB35006801  *

KEYS
(2) 02XR35005701
(2) 02XR45006502

ROLL PIN
(2) AX14CA064
(2) AX14CA096

IMPELLER NOSE PIECE
02XR35008701
02XR45009201

IMPELLER CAP SCREW
AA44AA269
AA44AA267

IMPELLER WASHER
02XB05002701
02XB05002702

SHIM
02XR35008601
02XB35006901  *

IMPELLER
CONTACT RCD
CONTACT RCD

Table 1 Large Diameter Parts List

