�Purpose:

To advise the field of a possible problem when the following symptoms are found when troubleshooting the 23XL with the TD6 compressor and frame 4 heat exchangers for:



Low discharge superheat

High level of refrigerant and oil level in the separator





Information:



As a method of noise abatement on the 23XL with TD6 compressors a small amount of liquid refrigerant is injected into the first closed lobe of the rotors. The amount of refrigerant is controlled by a metering .129” orifice located in the 3/8 inch copper line which feeds the refrigerant from the condenser to the compressor. Recently during lab testing the symptoms described above were discovered. While troubleshooting the problem it was discovered that the orifice had been damaged during the brazing process of the line. The joint which encapsulated the orifice was overheated and partially melted the orifice which was made out of aluminum. With the basic elimination of the orifice the amount of refrigerant is significantly increased. The increased amount of liquid can no longer be flashed during the compression process such that liquid is pumped through the rotors of the screw compressor. This refrigerant quenches the discharge causing the low discharge gas superheat. The liquid refrigerant and oil mixture passing through the compressor will not separate in the oil separator which accounts for the elevated level in the oil separator.      

.



Action:



If the chiller displays the symptoms described above, after isolating the refrigerant, disassemble the line where the orifice is located (see figure below) and replace the orifice with a new one available through RCD. The part number is AU53VA061. Avoid direct heat on the orifice and use a lower temperature brazing alloy such as 40% silver cadmium free.

� EMBED Word.Picture.6  ���



liquid injection orifice part numberAU53VA061







� EMBED Word.Picture.6  ���



Orifice AU53VA061�SERVICE BULLETIN DISTRIBUTION



BULLETIN NAME: Liquid Injection Orifice 



BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9�902



AUTHOR:  Benny DiMarco



COLLS:

	MODEL CODE:	23 Series

	KEY WORDS:	Orifice



��Mail Key�COIN�cc:Mail��X�DOMESTIC SERVICE PERSONNEL

   BSS Regional Operations Managers

   BSS Area Managers

   BSS Account Executives

   BSS Technical Consultants

   BSS Service Offices

   BSS Regional General Managers

   BSS Service Managers and Mechanics�

2.40A

2.40B

2.40D

2.40M

-

2.40

2.46A�

#BSS-ROM

-

-

#CBSTSE

#BSSSVC

#BSS-RGM

-���X�INTERNATIONAL SERVICE PERSONNEL

   International Service Managers

   Miscellaneous Service Personnel�

5.25G

2.33A�

#SBMISC

#SBMISC����DOMESTIC SALES PERSONNEL

   Canadian Field Sales

   BSS/ESS Sales/Managers



(Service Bulletins which relate to application)�

2.44

2.40L�

#CSD-CND

#BSSESS����INTERNATIONAL SALES PERSONNEL

   International Marketing Managers



(Service Bulletins which relate to application)�

5.25C�

#CIC-ASC���X�SPECIAL DISTRIBUTION

   CAES Products, Service & SO Engineers

   Miscellaneous Eng, Mktg, RCD Personnel�

2.33B

2.33D�

#SBMISC���

� REF number \* MERGEFORMAT �C9� - � REF title \* MERGEFORMAT �Liquid Injection Orifice  �

Page � PAGE �1�





Liquid Injection Orifice  ��C9902����3/9/99����New���23XL With TD6 Compressors and Frame 4 Heat Exchangers��N/A��



File:  Compressor, Motor, Drive, Gear���������Benny DiMarco���Alan M. Johnson������Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G��



� REF number \* MERGEFORMAT �C9� - � REF title \* MERGEFORMAT �Liquid Injection Orifice  �

Page � PAGE �2�





Title��Number����Date����S/S�����Date��



File:  ���������Benny DiMarco���Alan M. Johnson������Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G��
















