�
Purpose:





To define the “shielded cable” grounding requirement for the PIC communications cable on field wired free standing, or re-mounted unit, starters.





Reference:





Background:


The shielded communications cable, which runs from terminals A, B, C of terminal strip TB5 in the starter to terminals A, B, C in the machine power panel has occasionally been grounded at both ends of the cable shielding:   Grounding both ends of the communications cable shielding establishes a ground loop circuit which can induce spurious communications signals, causing nuisance shutdowns.





Requirement:


The communications cable shielding is to be grounded, at one end only, in the starter.











The adjacent label is attached


to the machine power panel as


reminder to ground only one


end of cable shielding, at the


starter.





	


�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  PIC Communications Interruption





BULLETIN NUMBER:  C9905





AUTHOR:  Mike Grimshaw





COLLS:


	MODEL CODE: 23XL


	KEY WORDS:Controls, Starter, Wiring 





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT � �


Page � PAGE �3�








 PIC Communications Interruption�
�
C9905�
�
�
�
01/28/99�
�
              19XL, XR, XRT, 23XL with Field Unit�
�
New�
�
�
Mounted, or Free Standing, Starters�
�
N/A�
�






File: Controls, Starter, Wiring�
�
�
�
�
�
�
�
�
Mike Grimshaw�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT � �


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























