�



Purpose:


To provide information to the field about the latest versions of software for the various models and the use of PSIO II (HK50AA023) modules only for replacement or software downloading.





Information:


The current part numbers for software are listed below.


�
Software�
�
�



Model�



Version�
Implementation Date ‡�
PSIO II 


Part Number�
�
17EX/FA�
02�
10/18/97�
17EX54001801�
�
19EX/EF/FA�
03�
1/8/96�
19EX54001901�
�
19XL/XT�
11�
1/14/97�
19XB04008911 §�
�
19XR/XRT †�
02�
1/13/97�
19XR04006001�
�
19XR (Frame 5 Compressor Only)�
03�
10/24/97�
19XR54004601�
�
23XL�
15 *�
4/14/97�
23XL04007215 ¤�
�
Notes:


‡  -	Date that appears on the label of the downloaded module.


† -	RCD is shipping replacement modules with Version 03 software only for all 19XR machines. 


* - 	When using a 23XL PSIO module with software version 14 or higher, to replace an earlier version, wiring modifications must be performed.  Instructions are included with the replacement module.  Instructions were also sent to the field as Service Bulletin C9605, dated 1/25/96. 


§ - 	RCD has been supplying replacement modules under 19XB04008911 since the introduction of version 11 software.  The factory was shipping version 11 software in new machines under 19XB04008501 since 1/14/97.  As of 2/15/99 the factory will be shipping machines with version 11 software under 19XB04008911.


¤ - 	RCD has been supplying replacement modules under 23XL04007215 since the introduction of version 15 software. The factory was shipping version 15 software in new machines under 23XL04007001 since 4/14/97.  As of 2/15/99 the factory will be shipping machines with version 15 software under 23XL04007215.








The PSIO supplier is no longer producing PSIO I (HK50AA020) modules.  All replacement modules shipped from RCD will be PSIO II (HK50AA023).  If a PSIO I module is in need of software for corruption reasons, the field should consider replacing the PSIO I with a PSIO II module.





The original service bulletin C9603, stated all 17EX and 17FA chiller with PIC controls shipped from the factory prior to 01/01/96 should be replaced with the latest software.  If these machines do not have at least version 1 software, dated 1/8/96, they should be updated.





Other service bulletins have addressed the software changes, and are listed below.





Product�
Bulletin Number�
Bulletin Title�
�
17EX,FA�
C9617�
17EX/FA VERSION 1 SOFTWARE�
�
19EF,EX,FA�
C9612�
19EF/EX/FA VERSION 3 SOFTWARE�
�
19XL/XT�
C9306�
19XL PSIO SOFTWARE VERSION 7�
�
�
C9409�
19XL PSIO SOFTWARE VERSION 9�
�
�
C9610�
VERSION 10 SOFTWARE�
�
�
C9725�
19XL VERSION 11 SOFTWARE�
�
23XL�
C9604�
VERSION 14 SOFTWARE FOR 23XL�
�
�
C9721�
23XL VERSION 15 SOFTWARE�
�






� REF number \* MERGEFORMAT �C9906   � - � REF title \* MERGEFORMAT �PSIO II Hardware and Software Part Numbers�


Page � PAGE �2�








PSIO II Hardware and Software Part Numbers�
�
C9906    �
�
�
�
2/1/99�
�
�
�
C9811�
�
�
17EX/FA, 19EF/EX/FA/XL/XR/XRT/XT, 23XL�
�
5/20/98�
�






File:  Controls & Wiring�
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�












