�
Purpose:





To define the 23XL capacity slide rod standardization to all C & D frame compressors, including “fixed” and “variable” V.I. configurations.





Reference:


	Bulletin C9709 - Frame 4 Slide Rod Change


	Bulletin C9803 - Slide Valve Rework Procedure;


	Bulletin C9827 - Capacity Slide Rod Surface Finish Requirements





Background:


Bulletin C9709 detailed the D Frame, fixed V.I. compressor capacity slide rod product improvement in April, 1997.   A new design capacity slide rod with “locking collars” replaced the original “keyed” capacity slide rod with tab washer and locknuts on D frame (4) “fixed” V.I. 23XL compressors.





This product change has been expanded to all frame 23XL compressors, including both “fixed” and “variable” V.I. configurations, as of October, 1997.





Requirement:


When ordering a replacement capacity slide rod for an older 23XL compressor, the capacity slide rod you receive will be the new design.  The new style locking collars must be used with the new slide rod.   Additionally, if the compressor is a variable Vi design, a new valve stop and spacer will be required to compensate for the larger size of the locking collars.   The attached chart correlates the “old” capacity rod part numbers to the new capacity rod, locking collar, valve stop and spacer part numbers for all fixed and variable V.I. compressors.





Parts Ordering:


Refer to the Capacity Rod Standardization Information spreadsheet for the new parts required with capacity rod change.   RCD has superseded the  “OLD” capacity slide rods to the new design.   The new style locking collars are ordered separately from RCD.


Loctite 603:  Loctite P/N 21440 for 10ml bottle.


                     Acceptable Substitute:  Loctite 609 & 675





Assembly Procedure:


1) Apply 3 drops of green loctite (Retaining Compound) to the male 


    threads, on both ends of the capacity rod, at 120 degree increments.


2) Remove the 4 set screws from both locking collars.   Install both 


    locking collars and torque the main body to 75 ft-lb. (102 Nm).   Two 


    locking collar sockets P/N TS-144504D (see sketch) will be required.


3) Apply 1 drop of green loctite on each set screw and reinstall set screws


    into the body of the two locking collars.


4) Torque the four set screws, in an even pattern, to 32 in-lb. (4Nm).





	Note: Make sure all parts are cleaned and degreased per Loctite’s


                    instructions.











�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:  Capacity Slide Rod Standardization





BULLETIN NUMBER:  C9908





AUTHOR:  Mike Grimshaw





COLLS:


	MODEL CODE: 23XL


	KEY WORDS:compressr, maint, servparts 





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT � �


Page � PAGE �1�








 Capacity Slide Rod Standardization�
�
C9908�
�
�
�
02/24/99�
�
 All 23XL Compressor Frame Sizes�
�
C9709�
�
�
Both Fixed & Variable V.I. Configurations�
�
4/15/97�
�






File:  Compressor, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Mike Grimshaw�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






Capacity Slide Rod Standardization


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























