�
Purpose:





To inform the field of a change to the shaft seal for the 17DA, 17FA, and 17MA,PA,SA compressors.





Information:





In late 1982, the shaft seal design was improved on the affected compressors.  This design change required the shaft geometry to change in the contact ring area of the low speed seal.  The O-ring that seals the ID of the Contact Ring was changed to a Quad-ring.  A redesign of the groove was necessary and it was moved outward from the shaft shoulder. The change in the location of the sealing ring groove required a change in the Contact Ring for the FA and DA compressors compressor because the keyway in the original Contact Ring would interfere with the new  seal ring location. 





If the shaft on a pre-1982 compressor must be replaced, the replacement would be the new design.  





The following figures show the changes on the various compressors and give the correct Quad-Ring and Contact Ring part numbers, where applicable.  Because shafts are often special on open drive compressors and even the standard shafts vary with coupling size, part numbers for shafts should be obtained from RCD for the specific machine serial number.





The FA compressor described is the original 17FA compressor with internal gears.   The 17EF, 17EX the 17FA with External gears (the “R-22” compressor) and the 17FX compressor all resemble the original 17FA but this bulletin does not apply to any of those.























� EMBED PBrush  ���








Compressor Frame�
New Contact Ring


�
Quad Ring


.�
�
17FA4�
17FA402-3022�
KK74ZW250�
�
17FA5�
17FA502-3022�
KK74ZW300�
�
�
�
�
�










































As shown in the following diagram, in the 17MA, PA, SA compressor, the O-ring the seals around the contact sleeve was replaced by a Quad-ring.  In the 40-size compressor, the O-ring that seals around the Contact Sleeve was also replaced by a Quad-ring.





Compressor frame�
Contact ring O-ring�
Contact Sleeve O-ring�
�
17MA, PA 30�
KK74ZW250�
N/A�
�
17SA 30�
KK74ZW236�
N/A�
�
17MA, PA, SA 40�
KK74ZW236�
KK71GW049�
�
�
�
�
�















 


� EMBED PBrush  ���























For both the 17DA7 and 8 compressors the sealing ring under the Rotating Contact Ring was changed to a Quad-Ring.  The rotating contact ring was changed because of the relocation of its keyway to accommodate the Quad-ring groove.





The parts are identical for both the 7 & 8 frame size 17DA.


This change applies to the design 2 seal assembly only as the Design 1 went out of production when the Design 2 was introduced into production.





Design 2 machines have the movable shaft position and the Teflon( shutdown seal.

















�


�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME: Shaft Seal O-ring to Quad Ring Change





BULLETIN NUMBER:  � REF number \* MERGEFORMAT �C9910  �





AUTHOR:  Ted Libera





COLLS:


	MODEL CODE:	� REF units \* MERGEFORMAT �17DA, 17FA, 17MA,PA,SA  �


	KEY WORDS:	 PARTS, SHAFT, SEAL





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9910  � - � REF title \* MERGEFORMAT �Error! Reference source not found.�


Page � PAGE �5�








�PAGE  �








�PAGE  �2�








Shaft Seal O-ring to Quad Ring Change�
�
C9910  �
�
�
�
02/26/99�
�
�
�
New�
�
�
17DA, 17FA, 17MA,PA,SA  �
�
N/A�
�






File:  Specified Parts�
�
�
�
�
�
�
�
�
Ted Libera�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9910  � - Shaft Seal O-ring to Quad Ring Change











Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Tom Pietrowicz�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























