�
Purpose:


To advise the field of a possible problem of a “Low Oil Pressure” alarm on 19XR centrifugal chillers with PIC II controls.








Information:





There have been reports of 19XR chillers going down on a low oil pressure alarm soon after start up.  Typically oil pressure of 24 to 28 PSID is established during the prelube cycle.  The chiller initiates a start, continues to operate through transition and then anywhere between 30 to 90 seconds into the start, before the guide vanes start to open, it may go down on low oil pressure.  The oil pressure loss experienced can be of three forms:


A momentary loss of oil pressure characterized by a quick dip in oil pressure as a result of some cavitation at the inlet of the pump or another transient occurring during start up causes an alarm.  The PIC II controls are able to recognize a loss of oil pressure with a duration of approximately one half of a second.


Gradual loss of oil pressure that can be tracked using the CVC screen causes an alarm.  After the chiller starts a small drop occurs down to about 21 PSID, continues past the alert level of 18 PSID to the alarm level of 15 PSID where the chiller shuts down on low oil pressure.


The third form is a hybrid of the first two where after start up the pressure difference gradually decreases and then dips momentarily as described in number 1.





Action:


Product engineering is investigating the root cause of the problem.  In the mean time it has been found that installing a refrigeration hose filled with oil between the oil sump and oil pump discharge transducers and the Schrader ports helps smooth out the transients so that the controls do not react to them.  This can be done until a permanent solution is found.  Please report the problem to Service Engineering and other temporary solutions can be discussed if this is not successful.








�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME: Low Oil Pressure Alarm





BULLETIN NUMBER:  C9912





AUTHOR:  Benny DiMarco





COLLS:


	MODEL CODE:	19XR Series


	KEY WORDS:	Oil Pressure





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C98� - � REF title \* MERGEFORMAT �Low Oil Pressure Alarms�


Page � PAGE �1�








Low Oil Pressure Alarms�
�
C9912�
�
�
�
4/9/99�
�
�
�
New�
�
�
19XR Series Chillers�
�
N/A�
�






File:  Installation, Start-Up & Operation�
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 5.25G�
�






� REF number \* MERGEFORMAT �C98� - � REF title \* MERGEFORMAT �Low Oil Pressure Alarms�


Page � PAGE �1�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























