�
Purpose:


To advise the field that a separate motor drain line orifice is not utilized or necessary on the 19XR frame 2,3,4 and 5 size compressors.





Information:


Several inquires have been received regarding the lack of the motor drain line orifice on 19XR centrifugal chillers.





On the 19XL series a separate orifice was used to keep the motor housing pressure elevated as compared to the cooler.  With the transmission being vented to the cooler this allows the motor housing pressure to be maintained at a higher level than the transmission.  The pressure differential between motor and transmission keeps oil that is being fed to the motor bearing from escaping into the motor shell and promotes the return of oil to the sump of the compressor. 





 On the 19XR centrifugal chillers the motor casting is machined to provide a restriction in the drain.  The separate orifice is not necessary.  Also, the transmission is vented to the downstream side of the inlet guide vanes, the lowest pressure in the system.  The transmission is kept at a lower pressure than the motor housing by virtue of both the built in orifice in the motor housing drain and the venting of the transmission housing.











Action:


If a tear down is necessary which requires the disassembly and the assembly  of the motor cooling drain DO NOT install any type of orifice in the drain line.  Reassemble the drain line with the same hardware found in the machine as shipped. 











�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME:Motor Drain Line Orifice 





BULLETIN NUMBER:  C9913 





AUTHOR:  Benny DiMarco





COLLS:


	MODEL CODE:	19XR Series


	KEY WORDS:	Motor; Orifice





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �C9� - � REF title \* MERGEFORMAT �Motor Drain Line Orifice�


Page � PAGE �1�








Motor Drain Line Orifice�
�
C9913�
�
�
�
4/20/99�
�
�
�
New�
�
�
19XR Frame 2,3,4 and 5 Compressors�
�
N/A�
�






File:  Compressor, Motor, Drive, Gear�
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�






� REF number \* MERGEFORMAT �C9� - � REF title \* MERGEFORMAT �Motor Drain Line Orifice�


Page � PAGE �2�








Title�
�
Number�
�
�
�
Date�
�
�
�
S/S�
�
�
�
�
Date�
�






File:  �
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�
























