Purpose:


To advise the field of a possible shock hazard due to residual voltage at motor terminals on hermetic motors. 








Information:





There have been reports from the field and from the lab of  electrical shocks from the motor terminals of the hermetic motors used on the 19XR series machines. These shocks may occur during servicing of  compressors or starters up to an hour or more after the electrical disconnects are opened.





The stored charge is a result of the polar nature of motor insulation materials and very high resistance. The voltage potential has been measured on several  occasions to be in excess of  100 volts which is high enough to startle and potentially injure someone as a direct or indirect result of the shock.





Action:





Whenever working on a motor or starter which is connected to the motor,open all disconnects and short each terminal to ground to dissipate the retained charge. The ground must be left in place until all service work is complete because the voltage may reappear after a momentary grounding of the terminals.





The ground wires must be removed before reapplying voltage.


� EMBED Word.Picture.6  ���


! WARNING





�
SERVICE BULLETIN DISTRIBUTION





BULLETIN NAME: Retained Motor Voltage





BULLETIN NUMBER:  C9916





AUTHOR:  Benny DiMarco





COLLS:


	MODEL CODE:	19 Series


	KEY WORDS:	Voltage, shock





�
�
Mail Key�
COIN�
cc:Mail�
�
X�
DOMESTIC SERVICE PERSONNEL


   BSS Regional Operations Managers


   BSS Area Managers


   BSS Account Executives


   BSS Technical Consultants


   BSS Service Offices


   BSS Regional General Managers


   BSS Service Managers and Mechanics�



2.40A


2.40B


2.40D


2.40M


-


2.40


2.46A�



#BSS-ROM


-


-


#CBSTSE


#BSSSVC


#BSS-RGM


-�
�
�
X�
INTERNATIONAL SERVICE PERSONNEL


   International Service Managers


   Miscellaneous Service Personnel�



5.25G


2.33A�



#SBMISC


#SBMISC�
�
�
�
DOMESTIC SALES PERSONNEL


   Canadian Field Sales


   BSS/ESS Sales/Managers





(Service Bulletins which relate to application)�



2.44


2.40L�



#CSD-CND


#BSSESS�
�
�
�
INTERNATIONAL SALES PERSONNEL


   International Marketing Managers





(Service Bulletins which relate to application)�



5.25C�



#CIC-ASC�
�
�
X�
SPECIAL DISTRIBUTION


   CAES Products, Service & SO Engineers


   Miscellaneous Eng, Mktg, RCD Personnel�



2.33B


2.33D�



#SBMISC�
�
�



� REF number \* MERGEFORMAT �Error! Reference source not found.� - � REF title \* MERGEFORMAT �Error! Reference source not found.�


Page � PAGE �2�




















Retained Motor Voltage �
�
C9916�
�
�
�
� DATE  \l �8/10/99��
�
�
�
New�
�
�
19XR Series Chillers�
�
New�
�






File:  Compressors, Motor, Drive, Gears�
�
�
�
�
�
�
�
�
Benny DiMarco�
�
�
Alan M. Johnson�
�
�
�
�
�
Mail Keys:  2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G�
�



























