

BULLETIN

Carrier Corporation


North American Operations



Number:
C9921
Date:
11/16/99
Supersedes:
C9718
Date:
10/30/97

Title:
19XR HIGH SPEED SHAFT CHANGE

Category:
GENERAL
Termination Date:


Author:
ALAN JOHNSON



Dept:
CSS Service Engineering





Models Affected:
CAC:  19XR Frame 3 and 4

BDP:  




PURPOSE:

To inform the field of a change in the diameter of the high speed shafts on frame 3 and frame 4 19XR compressors.

NOTE:

This bulletin has been revised to correct part number errors.  Numbers with a * have



been corrected.

GENERAL INFORMATION:

The frame three and frame four 19XR compressors were released with a high speed shaft that measured 1.15 inches at the impeller mounting end of the shaft. To increase the overall strength of the shaft for higher tonnages the diameter was changed to 1.37 inches. Approximately 8/97 all production units utilized the new large diameter shaft.

SERVICE PARTS

Service parts only stocks the new larger diameter shaft and associated impellers. Before ordering replacement parts it will be necessary to check the diameter of the shaft (see figure 1) (i.e. if the machine has a small diameter shaft and either the shaft or impeller needs to be replaced, a new shaft, impeller,  spacer, and shim pack, etc. will need to be ordered).

(SEE SHAFT ON HARD COPY)

Figure 1. High Speed Shaft

The table below contains the large diameter high speed assembly part numbers along with the other associated parts that will need to be ordered if replacing a small diameter with a large diameter. The large diameter shaft will work with a small diameter thrust housing assembly.

PART NAME
FRAME 3 COMPRESSOR
FRAME 4 COMPRESSOR 

HI SPD BRG & SHAFT ASSY 60 HZ
02XR34000201
02XR44000701

HI SPD BRG & SHAFT ASSY 50 HZ
02XR34000202
02XR44000702  *

INCLUDES:




HIGH SPEED SHAFT 60 HZ
02XR35008401
02XR45008601


HIGH SPEED SHAFT 50 HZ
02XR35008402
02XR45008602

SPACER
02XB35006801  *
02XB35006801  *

KEYS
02XR35005701 (2)
02XR45006502 (2)

ROLL PIN
AX14CA064 (2)
AX14CA096 (2)

IMPELLER NOSE PIECE
02XR35008701
02XR45009201

IMPELLER CAP SCREW
AA44AA269
AA44AA267

IMPELLER WASHER
02XB05002701
02XB05002702

SHIM
02XR35008601
02XB35006901  *

IMPELLER
CONTACT RCD
CONTACT RCD

Table 1 Large Diameter Parts List

Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















