

BULLETIN

Carrier Corporation


North American Operations



Number:
C0009
Date:
7/21/00
Supersedes:

Date:


Title:
PIC Thermistor Thermowells

Category:
Controls / Wiring
Termination Date:


Author:
Ted Libera



Reviewed by:
Alan M. Johnson



Dept:
CSS Service Engineering





Models:

Affected:
CAC:  All PIC-Equipped Chillers 

BDP:  







PURPOSE:

To inform the field of a set of thermowells that can be used with the standard PIC thermistors and can 

be inserted in the existing thermistor connections

INFORMATION:

Carrier Transicold Marine Division designed these thermowells to satisfy requests from its marine customers.  They are now available through RCD.   

To install, remove the sensor from its position, install the well in its place then install the sensor into the well. 

Cooler Nozzles In & Out:


P/N 90C02-3932-1  Material = 316SS

Condenser Nozzles In & Out: 


P/N 90C02-3932-2  Material = 90/10 Cu-Ni 


Dimensionally Identical to “-1”

Compressor Oil Temperature:


P/N 90C02-3932-3  Material = 316SS

Compressor Discharge Temperature:


P/N 90C02-3932-4  Material = 316SS
















Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















