

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0103A
	Date:
	10/8/01
	Supersedes:
	C01013
	Date:
	2/26/01

	Title:
	ISM Transition with Wye-Delta Starter

	Category:
	GENERAL
	Termination Date:
	

	Author:
	Scott Nieforth
	
	

	Reviewed by:
	Alan M. Johnson
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  19XR, 19XRT and 23XL with PIC-II controls

BDP:  

	
	Purpose:

This bulletin explains the transition sequence of the ISM when used with a Wye-Delta starter.

Information:

The ISM will go to Transition mode during the time interval between 5 and 20 seconds following 1 CR relay closure if the following conditions are simultaneously met:

· The 1M Auxiliary contacts remain closed

· The motor current is between 5% RLA and 90% RLA

· No Starter Faults exist

The ISM will go to Transition mode if more than 20 seconds have elapsed following 1 CR relay closure if the following conditions are simultaneously met:

· The 1M Auxiliary contacts remain closed

· The motor current is between 5% RLA and 150% RLA

·  No Starter Faults exist

Post Transition Faults (Time limits are not configurable):
·   A 2M Contact Fault(State 201) will result after Transition mode if all of the following conditions are true:

· One second has elapsed since the Transition relay has closed

· The 2M Auxiliary relay does not remain closed

·   An  Excess Acceleration Time Fault(State 203) will result if all of the following conditions are true:

· More than 20 seconds have elapsed since the 1CR relay has closed

· Motor current has not fallen below 150% RLA.

·   An  Excess Acceleration Time Fault(State 203) will also result if all of the following conditions are true:

· More than 45 seconds have elapsed since the 1CR relay has closed

· Motor current has not fallen below 100% RLA.

File:   Controls and Wiring



	
	











Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















