

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0107
	Date:
	3/5/01
	Supersedes:
	C9921
	Date:
	11/16/99

	Title:
	19XR Hi-Speed Shaft and Labyrinth Change

	Category:
	GENERAL
	Termination Date:
	

	Author:
	Matt Canino
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC: 19XR Frame 3 & 4

BDP:  


PURPOSE:

C9921 informed the field of a change in the diameter of the high speed shafts on frame 3 and frame 4 19XR compressors.  This revision provides information about the high speed labyrinth part numbers (for Frame 3 compressors only).  See Table 2 and Bulletin C9812.

GENERAL INFORMATION:

The frame 3 and frame 4 19XR compressors were released with a high-speed shaft that measured 1.15 inches at the impeller mounting end of the shaft. To increase the overall strength of the shaft for higher capacities the diameter was changed to 1.37 inches. Approximately 8/97 all production units utilized the new large diameter shaft.  Soon after the shaft diameter change the Frame 3 labyrinth changed as shown in Table 2 and Bulletin C9812.

SERVICE PARTS

Service parts only stocks the new larger diameter shaft and associated impellers. Before ordering replacement parts it will be necessary to check the diameter of the shaft (see figure 1) (i.e. if the machine has a small diameter shaft and either the shaft or impeller needs to be replaced, a new shaft, impeller, spacer, and shim pack, etc. will need to be ordered).

FILE:
Compressor, Motor, Drive, Gears

[image: image1.png]B 1 IF DIMENSION "C* = 1.37° YOU HAVE THE LARGER
| == DIAMETER SHAFT

IF DIMENSION “C" = 1.15° YOU HAVE THE SMALLER
DIMENSION *C* DIAMETER SHAFT

IMPELLER SHAFT—/




Figure 1. High Speed Shaft

The table below contains the large diameter high speed assembly part numbers along with the other associated parts that will need to be ordered if replacing a small diameter with a large diameter. The large diameter shaft will work with a thrust housing assembly that had a small diameter shaft.

	PART NAME
	FRAME 3 COMPRESSOR
	FRAME 4 COMPRESSOR 

	HI SPD BRG & SHAFT ASSY 60 HZ
	02XR34000201
	02XR44000701

	HI SPD BRG & SHAFT ASSY 50 HZ
	02XR34000202
	02XR44000702 

	INCLUDES:
	
	

	
HIGH SPEED SHAFT 60 HZ
	02XR35008401
	02XR45008601

	
HIGH SPEED SHAFT 50 HZ
	02XR35008402
	02XR45008602

	SPACER
	02XB35006801  *
	02XB35006801 

	KEYS
	02XR35005701 (2)
	02XR45006502 (2)

	ROLL PIN
	AX14CA064 (2)
	AX14CA096 (2)

	IMPELLER NOSE PIECE
	02XR35008701
	02XR45009201

	IMPELLER CAP SCREW
	AA44AA269
	AA44AA267

	IMPELLER WASHER
	02XB05002701
	02XB05002702

	SHIM
	02XR35008601
	02XB35006901 

	IMPELLER
	CONTACT RCD
	CONTACT RCD


Table 1 Large Diameter Parts List

For Frame 3 Compressor Balance Piston Labyrinth part numbers, refer to the table below:

	
	OLD
	NEW

	Compressor 

Code
	Balance Piston Labyrinth
	OD in. (mm)
	Balance Piston Labyrinth
	OD in. (mm)

	323, 333, 343, 353, 363, 373, 383
	
	
	
	

	324, 334, 344, 354, 364, 374, 384
	19XR660010
	6.292/6.290

(159.8/159.7)
	19XR660034
	6.192/6.190

(157.3/157.2)

	325, 335, 345, 355, 365, 375, 385
	
	
	
	


Table 2 Balance Piston Labyrinth Parts List










Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















