

BULLETIN

Carrier Corporation


North American Operations



	Number:
	C0108
	Date:
	3/5/01
	Supersedes:
	
	Date:
	

	Title:
	23XL Oil Separator and Corresponding Machine Assemble Changes 

	Category:
	GENERAL
	Termination Date:
	

	Author:
	David Jensen
	
	

	Dept:
	CSS Service Engineering
	
	

	

	Models Affected:
	CAC:  23XL
BDP:  


Purpose:

This bulletin will describes the changes to the 23XLI and 23XLII oil separators and machine assemblies which coincide with the change to Howden compressors covered in bulletin #C0102.

Summary:

In the beginning of March 2000 changes were made to the 23XL machine assembly and oil separator designs for both the 23XLI (frame 1&2) and 23XLII (frame 3&4). 

23XLI (Frame 1 and 2 Heat Exchangers)
The 23XLI major component changes were implemented on units produced in March 2000. The first major component change was eliminating the external oil sump, which was located on the condenser. The sump was incorporated into the bottom of the oil separator vessel increasing the height by 5.5 inches. The elimination of the external sump required adding an external oil filter assembly that includes a canister type housing and necessary plumbing to complete the lube system. See the diagram below for a visual reference. These changes can be used to visually identify a 23XLI with these enhancements.  

	[image: image1.wmf]OIL FILTER

7'-3 1/8"

[2213mm]

OVERALL HEIGHT

MACHINE

COMPRESSOR END

C

L

DRIVE END

COND.

REAR VIEW


	[image: image2.wmf]REAR VIEW

6'-9 5/8"

[2073mm]

COND.

C

L

DRIVE END

COMPRESSOR END

MACH.

OVERALL

HEIGHT

External Oil Sump



	Production Units After 03/2000
	Production Units Before 3/2000


FILE:
Installation, Start-up, Operation

23XLII (Frame 3 and 4 Heat Exchangers)

On the larger 23XLII machines several new heat exchanger sizes were added to accommodate efficiency requirements. Available now are heat exchanger sizes 30-34(10ft length), 40-43 (12ft length) and 45-48 (14ft length).  Below are illustrations that show the different unit sizes.

	[image: image3.wmf]10'-0"

[3048mm]

C

L

C

L

OIL SEP.

COMPRESSOR END

COND.

C

L

L

C

L

C

L

C

DRIVE END

REAR VIEW


	[image: image4.wmf]REAR VIEW

DRIVE END

C

L

C

L

L

C

COND.

COMPRESSOR END

OIL SEP.

L

C

L

C

[3747mm]

12'-3 1/2"



	23XLII Heat Exchanger Frame 30-33 

(10ft Length)
	23XLII Heat Exchanger Frame 40-43 

(12ft Length)


	[image: image5.wmf]C

L

COMPRESSOR END

[4267mm]

14'-0"

L

C

C

L

COND.

L

C

L

C

C

L

REAR VIEW

DRIVE END

OIL SEP.



	23XLII Heat Exchanger Frame 45-48 

(14ft Length)


Mail Keys: 2.33A, 2.33B, 2.33D, 2.40, 2.40A, 2.40B, 2.40D, 2.40M, 2.46A, 5.25G 


_988694773.doc
�



�
















